date axis tick marks at one day intervals

Graph of text file from data logger.  347905 points at one second intervals.

I don't understand how the LCW out temperature can drop below the LCW in temp.  I suspect the sensor fell off the pipe and is touching concrete.

Steel temperature recovers in half a day.  Ditto stand and air.

Concrete temperature is still coming down slowly after two days.  Could this be the source of the "inelasticity" see in the path length snapshots?  Pathlength did not restore to original level in the 24 hours between the time water temperature was dropped and Ops used the doglegs to flatten.