## Slide 1
POWER SUPPLY
EXTERNAL INTLCK CONTACTS
XXXX
XX
XXXXX
POWER SUPPLY
EXTERNAL INTLCK CONTACTS
Note: (label goes below “TM3 QUENCH DETECTOR UNIT: signal)
RELAY 1
LCW TEMPERATURE
TM0 – TM4
RELAY 2
PLC HARDWARE WATCHDOG
RELAY 3
WINDOW SHUTTER
TM0 – TM4
IN—CH0
IN—CH1
INTERLOCK
TERMINAL BLOCKS
IN—CH2
IN—CH3
IN—CH4
IN—CH5
IN—CH6
IN—CH7
NOT USED
NOT USED
IN—CH8
IN—CH9
IN—CH10
IN—CH11
IN—CH12
IN—CH13
IN—CH14
IN—CH15
1L+
1M
IN—CH16
IN—CH17
IN—CH18
IN—CH19
IN—CH20
IN—CH21
IN—CH22
IN—CH23
NOT USED
NOT USED
IN—CH24
IN—CH25
IN—CH26
IN—CH27
IN—CH28
IN—CH29
IN—CH30
IN—CH31
37
38
39
40
2L+
2M
INTERLOCK RELAYS
SIEMENS SIMATIC S7-1500
DI 32X24VDC HF (6ES7521-1BL00-0AB0)
DIGITAL INPUT MODULE
CHASSIS 1
SLOT 2
XXXXXX
XXXXXX
PLACE
XXXXXX
FOR ALL
4. 1L+ AND 2L+ ARE SUPPLY VOLTAGE 24 VDC
5. 1M AND 2M ARE GROUND
XXXX
XX
PLACE
XXXX
XX
FOR ALL
XXXX
XX
XXXX
XX
XXXXXX
RELAY 4
TM0 POWER SUPPLY
INTLCK STATUS
Need a total 24 Terminal Blocks one per interlock signal
Need a total 24 identical relays
Keep this extra TB but move it below the 24th terminal block
Do not need all these jumpers
RELAY 0
LCW FLOW
TM0 – TM4
RELAY 5
TM0
RTD CABLE DISCONNECTION
RELAY 6
TM0
VOLTAGE TAP CABLE DISCONNECTION
ALL TOROUS MAGNETS
RELAY 7
TM0
QUENCH DETECTOR UNITS
RELAY 8
TM1 POWER SUPPLY
INTLCK STATUS
RELAY 9
TM1
RTD CABLE DISCONNECTION
RELAY 10
TM1
VOLTAGE TAP CABLE DISCONNECTION
RELAY 11
TM1
QUENCH DETECTOR UNITS
Keep this WIRE but move it below the 24th INTERLOCK which will be TM3 QUENCH DETECTOR UNITS
RELAY 12
TM2 POWER SUPPLY
INTLCK STATUS
RELAY 13
TM2
RTD CABLE DISCONNECTION
RELAY 14
TM2
VOLTAGE TAP CABLE DISCONNECTION
RELAY 15
TM2
QUENCH DETECTOR UNITS
REPEAT THIS FOR SIGNALS FOR TM 3 AND TM4
Repeat this wiring with the two polygons per each interlock signal
SLOT 2 - DIGITAL INPUT MODULE
HALLL A
MOLLER
This wire “COM” goes to pin 20 and 40
XXXXXX
Put this in circles same as other channels
XXXXXX….XXXX