## Sheet1
Date: | 2017-02-20
By : | Pablo Campero
INSTRUMENTATION TEST PLC- EPICS PLAN
SOLENOID SERVICE TOWER - SST
Signal ID | Sensor Type | Calibrated - Tested | Installed | To be tested Now | To be Tested after | Action | Check | Comments
TR8622A | Cernox | No | Yes | Yes |  | 1. Verify hardwiring - Use reference DWG 0649 & 0678
TR8622Ar |  | No | Yes |  |  | 2. Check sensor connection in the Cryocon unit - Use Cryocon maps
TR8622B |  | Yes | Yes |  |  | 3. Unplug DB9 connectors except sensor that is being checked in rear panel of Cryocon 1
TR8622Br |  | No | Yes |  |  | 4. Verify if sensor position correspond to the channel assigned
TR8611 | [5 empty] | 5. Check communication between 490-NBX module and PLC
TR8611r | [5 empty] | 6. Verify correct read-back values for the sensor in the PLC controller
TR8672 | [5 empty] | 7. Check communication between PLC and EPICS
TR8672r | [5 empty] | 8. Use the Helium SST EPICS screen to verify and moniutor the temperature sensor readings in [K] units
TR8671 | [5 empty] | 9. Record Read-back values - compare PLC and Cryocon Readings
TR8671r | [5 empty] | 10. Repeat the steps above with each temperature sensor
TR8610
TR8610r
TR8670 | Cernox |  |  | Yes |  | 1. Verify hardwiring - Use reference DWG 0649 & 0678
TR8670r | [5 empty] | 2. Check sensor connection in the Cryocon unit - Use Cryocon maps
TR8673 | [5 empty] | 3. Unplug DB9 connectors except sensor that is being checked in rear panel of Cryocon2
TR8673r | [5 empty] | 4. Verify if sensor position correspond to the channel assigned
TR8674 | [5 empty] | 5. Check communication between 490-NBX module and PLC
TR8674r | [5 empty] | 6. Verify correct read-back values for the sensor in the PLC controller
TR8624A | [5 empty] | 7. Check communication between PLC and EPICS
TR8624B | [5 empty] | 8. Use the Helium SST EPICS screen to verify and moniutor the temperature sensor readings in [K] units
TP8621A | PT- 100 |  |  |  |  | 9. Record Read-back values - compare PLC and Cryocon Readings
TP8621Ar | [5 empty] | 10. Repeat the steps above with each temperature sensor
TP8621B
TP8621Br
TP8611 | PT- 100 |  |  | Yes |  | 1. Verify hardwiring - Use reference DWG 0649 & 0678
TP8611r | [5 empty] | 2. Check sensor connection in the Cryocon unit - Use Cryocon maps
TP8620A | [5 empty] | 3. Unplug DB9 connectors except sensor that is being checked in rear panel of Cryocon3
TP8620Ar | [5 empty] | 4. Verify if sensor position correspond to the channel assigned
TP8620B | [5 empty] | 5. Check communication between 490-NBX module and PLC
TP8620Br | [5 empty] | 6. Verify correct read-back values for the sensor in the PLC controller
TP8675 | [5 empty] | 7. Check communication between PLC and EPICS
TP8675r | [5 empty] | 8. Use the Helium SST EPICS screen to verify and moniutor the temperature sensor readings in [K] units.
TP8622A | [5 empty] | 9. Record Read-back values - compare PLC and Cryocon Readings
TP8622Ar | [5 empty] | 10. Repeat the steps above with each temperature sensor
TP8622B
TP8622Br
PT8620 | Pressure |  | Yes | Yes (Initial Test) |  | 1. Verify hardwiring - Use reference DWG 0626
PT8670 |  |  | Yes |  |  | 2. Ensure proper power source (24 VDC ) to the Pressure Transducers
PT8675A | [5 empty] | 3.Verify coinfiguration/ scaling factors PLC Input module
PT8677 | [5 empty] | 4. Verify correct read-back values for the sensor in the PLC controller
5. Check communication between PLC and EPICS
6. Use the Helium - SST EPICS screen to verify and monitor the pressure readings in Atma
7. Record Read-back values
8. Repeat the steps above with each Presure transducer
LL8620DP | Differential Pressure |  | Yes | Yes |  | 1. Verify hardwiring - Use reference DWG 0626
LL8670DP |  |  | Yes |  |  | 2. Ensure proper power source (24 VDC) to the DP
3.Verify coinfiguration/ scaling factors PLC module
4. Differential pressure transducer are used to mesurre LHe level in reservoirs/ check formula used in PLC logic
5. Verify correct read-back values for the sensor in the PLC controller
6. Check communication between PLC and EPICS
8. Use the Helium - SST EPICS screen to verify and monitor the LHE Liquid level SC in % units.
8. Record Read-back values
9. Repeat the steps above with each DP sensor
LL8629SC | Liquid Level |  | Yes | No |  | 1. Verify hardwiring - Use reference DWG 0659 & 0628 |  | Check with Dave K.
LL8670SC |  |  | Yes |  |  | 2. Ensure proper 24 VDC COM for the LL-SC sensors
3. Check configuration(Output signals, Set points, limit levels) in the AMI 135 controller - Use Level measurments on [%].
4.Verify coinfiguration/ scaling factors (0-10V) Analog Input PLC module
5. Differential pressure transducer are used to mesurre LHe level in reservoirs/ check cryo-formula used in PLC logic
6. Verify correct read-back values for the sensor in the PLC controller
7. Check communication between PLC and EPICS
8. Use the Helium - SST EPICS screen to verify and monitor the LHE Liquid level SC in % units.
8. Record Read-back values
9. Repeat the steps above with each LL-SC sensor
FI8621A | Flow Meters |  |  | No |  | 1. Verify hardwiring - Use reference DWG 0660, 0627 & 0624 |  | No flow at the moment
FI8621B | [5 empty] | 2. Ensure proper 24 VDC voltage source for the Mass Flow controller
3. Check configuration(Output/Input signals, Set points, limit levels) in the TELEDYNE Mass Flow controller
4. Verify coinfiguration/ scaling factors (4-20mA) Analog Output PLC module
5.Verify coinfiguration/ scaling factors (4-20mA) Analog Input PLC module
6. Verify correct read-back values for the sensor in the PLC controller
7. Check communication between PLC and EPICS
8. Use the Helium - SST EPICS screen to verify and monitor the Lead Flow in [SLPM] units.
8. Record Read-back values
9. Repeat the steps above with each flow meter
EV8611CD | EV- Valves |  | Yes | Yes |  | 1. Verify hardwiring - Use reference DWG 0638 & 0650
EV8670BY |  |  | Yes |  |  | 2. Ensure proper power source 24 V DC
EV8611JT |  |  | Yes |  |  | 3.Verify PLC Relay Outputs - configuration 0-24 VDC
EV8612 |  |  | Yes |  |  | 4.Verify configuration switch on the LVDT's that belongs to the valve respectevely - Use DWG 0661
EV8611CD_LVDT | LVDT's |  | Yes | Yes |  | 5. Check communication between PLC and EPICS
EV8670BY_LVDT |  |  | Yes |  |  | 6. Valves have a PID control/ Check Mode (Manual) to control OPEN/CLOSE
EV8611JT_LVDT |  |  | Yes |  |  | 7. Use PID Set parameters EPICS screen to set Normal mode and set point valve
EV8612_LVDT |  |  | Yes |  |  | 8. Force bit in the PLC expert screen to OPEN and CLOSE the Valves
9. Verify correct read-back values for LVDT'S the PLC controller
10. Ensure the correct PID response in the PLC logic.
11. Verify Relay output indicators to OPEN an CLOSE the valve
12. Use the Helium - SST EPICS screen to verify the % of open and close indicators in the valve
13. Record Read-back values
14. Repeat the steps above with each EV and LVDT
SV8622 | SV - Valves |  |  | Yes |  | 1. Verify hardwiring - Use reference DWG 0640
SV8678CR | [5 empty] | 2. Ensure proper power source 24 V DC
SV8678DV | [5 empty] | 3.Verify PLC Relay Outputs - configuration 0-24 VDC
SV8675BY | [5 empty] | 4. Force bit in the PLC expert screen to OPEN and CLOSE the Valve
5. Check communication between PLC and EPICS
6. Use the Helium - SST EPICS screen to verify the open/close valve indicators (Green - open)
7. Record Read-back values (OPEN/CLOSE)
8. Repeat the steps above with each SV
PV8674 | PV- Valve |  |  | Yes |  | 1. Verify hardwiring - Use reference DWG 0623
2. Ensure proper power source 24 V DC
3. Check pressure stable for the air supply in the valve
4.Verify Analog Outputs - configuration (0-10 v/4-20 mA)
5. Force bit in the PLC expert screen to OPEN and CLOSE the Valve
6. Check communication between PLC and EPICS
7. Use the Helium - SST EPICS screen to verify the open/close valve indicators (Green - open)
8. Record Read-back values (OPEN/CLOSE)
HT8621A | Heater |  |  | Yes (Initial test) |  | 1. Verify hardwiring - Use reference DWG 0638 |  | Check Power levels with Dave K.
HT8621B | [5 empty] | 2. Ensure proper power source 24 V DC
3.Verify Relay Outputs - configuration module
4.Check thresholds on the lead temperatures A and B.
5. Force bit in the PLC expert screen to turn ON/OFF the Heaters
6. Check communication between PLC and EPICS
7. Use the Helium - SST EPICS screen to verify ON/OFF heater indicators (Green light On)
8. Record Read-back values
9.. Repeat the steps above with each heater
HTR8620 | Heater |  |  | No |  | 1. Verify hardwiring - Use reference DWG 0638, 0664 & 0627 |  | Need to be Cold before checking. - Talk to Dave K. to confirm
HTR8672 | [5 empty] | 2. Ensure proper power source 120 VAC to the power supply Sorensen
3. Check configuration(Output signals, Set points, limit levels) in the SORENSEN DLM 600W power supply - Use 4-20 mA switch configuration
4. Verify coinfiguration/ Relay Output PLC module
5.Verify coinfiguration/ scaling factors (4-20mA) Analog Input PLC module
6. Check communication between PLC and EPICS
7. Heater has a PID control/ Check Mode (Manual) to control the heater
8. Use PID Set parameters EPICS screen to set Normal mode and set a test value for the Heater
9. Force bit in the PLC expert screen to turn ON/OFF the heater
10. Verify correct read-back values for volatge and current for the heaters in the PLC controller
11. Ensure the correct PID response in the PLC logic.
12. Verify Relay output indicators to ON/OFF
13. Use the Helium - SST EPICS screen to verify the Heater is ON OR OFF, check % read back values and compare with the set point
14. Record Read-back values
15. Repeat the steps above with each Heater
VACUUM SIGNALS
CG8606 | gauge |  |  | No |  | 1. Verify hardwiring - Use reference DWG 0628 & 0656 |  | Controller and Vacuum pump need to be operational first to test this signals
CG8600TB | [5 empty] | 2. Ensure proper 120 ADC voltage source for the Vacuum controller and Instrumentation
TB8600 (TURBO) | pump speed |  |  |  |  | 3. Check configuration(Analog output/Input signals, Set points, limit levels) in the PFIFER TPG 362 controller
4. Verify coinfiguration/ scaling factors (0-10 V) Analog Input PLC module
5. Verify correct read-back values for thegauges in the PLC controller
6. Check communication between PLC and EPICS
7. Use the Vaccum Sytem EPICS screen to verify and monitor vacum signals [Torr] units.
8. test Alarm handler for the vaccum threshold established - Use EPICS Handler
9. Record Read-back values
10. Repeat the steps above with each vacuum signal
PV8600 | PV- Valve |  |  | No |  | 1. Verify hardwiring - Use reference DWG 0641 & 0656 |  | Controller and Vacuum pump need to be operational first to test this signals
2. Ensure proper power source 24 V DC
3. Check pressure stable for the air supply in the valve
4.Verify Discrete Input PLC Module - configuration (0-30V)
5. In the PLC expert screen verify the readback switch position OPEN and CLOSE for the Valve
6. Check communication between PLC and EPICS
7. Use the Vaccum Sytem EPICS screen to verify and monitor the main vacum gate valve (OPEN/CLOSE)