## Solenoid Drawings List
2017-01-06
Drawing Number | Drawing Name | REV - | REV A | NOTES:
B00000-09-00-0600 | Solenoid Cryogenics P & I Diagram | IN WORK
B00000-09-00-0605 | Drawing List
B00000-09-00-0610 | System Overview
B00000-09-00-0611 | Rack Layout | IN WORK
B00000-09-00-0612
B00000-09-00-0613
B00000-09-00-0614
B00000-09-00-0615 | Ethernet Single Line | UNDEFINED
B00000-09-00-0616 | Serial Single Line | UNDEFINED
B00000-09-00-0617
B00000-09-00-0618
B00000-09-00-0619
B00000-09-00-0620 | Local Backpanel Assembly | COMPLETE
B00000-09-00-0621 | Local 24 VDC Power Source | COMPLETE
B00000-09-00-0622 | Local PLC Chassis Assembly | COMPLETE
B00000-09-00-0623 | Local Slot 1 - | COMPLETE
B00000-09-00-0624 | Local Slot 2 - | COMPLETE
B00000-09-00-0625 | Local Slot 3 - |  |  | PLACEHOLDER
B00000-09-00-0626 | Local Slot 4 - | COMPLETE
B00000-09-00-0627 | Local Slot 5 - | COMPLETE
B00000-09-00-0628 | Local Slot 6 - | COMPLETE
B00000-09-00-0629 | Local Slot 7 - |  |  | PLACEHOLDER
B00000-09-00-0630 | Local Slot 8 - | WEB+ |  | PLACEHOLDER
B00000-09-00-0631 | Local Slot 9 - | ETHERNET |  | PLACEHOLDER
B00000-09-00-0632
B00000-09-00-0633 | VT ISOAMP Sub-chassis (Machanical)
B00000-09-00-0634
B00000-09-00-0635 | Remote Backpanel Assembly | COMPLETE
B00000-09-00-0636 | Remote PLC Chassis Assembly | COMPLETE
B00000-09-00-0637 | Remote 24 VDC Power Source | IN WORK
B00000-09-00-0638 | Remote Slot 0 - | COMPLETE
B00000-09-00-0639 | Remote Slot 1 - | COMPLETE
B00000-09-00-0640 | Remote Slot 2 - | COMPLETE
B00000-09-00-0641 | Remote Slot 3 - | COMPLETE |  | PLACEHOLDER
B00000-09-00-0642 | Remote Slot 4 - | COMPLETE
B00000-09-00-0643 | Remote Slot 5 - | COMPLETE
B00000-09-00-0644 | Remote Slot 6 - |  |  | PLACEHOLDER
B00000-09-00-0645 | Remote Slot 7 - | COMPLETE
B00000-09-00-0646 | Remote Slot 8 - |  |  | PLACEHOLDER
B00000-09-00-0647 | Remote Slot 9 - | ETHERNET |  | PLACEHOLDER
B00000-09-00-0648 | Interconnect Panel Layout | COMPLETE
B00000-09-00-0649 | CRYOCON Termination & SOE Detail | COMPLETE
B00000-09-00-0650 | EV Relays (Sht 1 & 2) | COMPLETE
B00000-09-00-0651 | LVDT's | COMPLETE
B00000-09-00-0652 | EV & LVDT Cables | COMPLETE
B00000-09-00-0653 | Keep Alive Timing Relay Wiring | COMPLETE
B00000-09-00-0654 | Magnet Power Supply Connections | COMPLETE
B00000-09-00-0655 | Vacuum Controls Layout | IN WORK
B00000-09-00-0656 | Vacuum Interlock & Control Schematic | IN WORK
B00000-09-00-0657 | Vacuum Switch Panel Layout | IN WORK
B00000-09-00-0658 | Vacuum Turbo Control Panel Layout | COMPLETE
B00000-09-00-0659 | LHe & LN2 Liquid Level/DP Wiring | COMPLETE
B00000-09-00-0660 | Mass Flow Measurement | COMPLETE
B00000-09-00-0661 | Immersion Heater Wiring_8672/8601 | COMPLETE
B00000-09-00-0662 | Force Washer Load Cells | COMPLETE
B00000-09-00-0663 | Immersion Heater Wiring_8620/8623 | COMPLETE
B00000-09-00-0664 | Magnet Relief Sensor Wiring Diagrams | COMPLETE
B00000-09-00-0665 | Solenoid Sensor Wiring Diagrams #1 | COMPLETE
B00000-09-00-0666 | Solenoid Sensor Wiring Diagrams #2 | COMPLETE
B00000-09-00-0667 | Solenoid Sensor Wiring Diagrams #3 | COMPLETE
B00000-09-00-0668 | Solenoid Sensor Wiring Diagrams #4 | COMPLETE
B00000-09-00-0669 | Solenoid Sensor Wiring Diagrams #5 | COMPLETE
B00000-09-00-0670
B00000-09-00-0671
B00000-09-00-0672
B00000-09-00-0673
B00000-09-00-0674
B00000-09-00-0675
B00000-09-00-0676
B00000-09-00-0677 | Spares Sensor Wiring Diagrams | COMPLETE
B00000-09-00-0678 | Chimney Wiring & CRYOCONS | COMPLETE
B00000-09-00-0679 | VT Attenuator 24 VDC Power | COMPLETE
B00000-09-00-0680 | Voltage Tap System Diagram | COMPLETE
B00000-09-00-0681 | Voltage Tap Backpanel | COMPLETE
B00000-09-00-0682 | cRIO Sub-Chassis (Mechanical) | COMPLETE
B00000-09-00-0683 | VT Attenuator sub-chassis | COMPLETE
B00000-09-00-0684 | Voltage Tap Test Panel Assembly | COMPLETE
B00000-09-00-0685 | Voltage Tap Test Panel Mechanical | COMPLETE
B00000-09-00-0686 | Voltage Tap Test Panel Electrical | COMPLETE
B00000-09-00-0687 | Quench Detector Wiring | COMPLETE
B00000-09-00-0688 | cRIO RS-232 Wiring Detail | COMPLETE
B00000-09-00-0689 | cRIO 24VDC Wiring Drawing | COMPLETE
B00000-09-00-0690 | Resisitor Chassis Layout Mechanical | IN WORK
B00000-09-00-0691 | Resisitor Chassis Connector Panel | COMPLETE |  | MACHINE SHOP
B00000-09-00-0692
B00000-09-00-0693
B00000-09-00-0694 | Small Resistor Board (2) | IN WORK
B00000-09-00-0695 | Large Resistor Board (2) | IN WORK
B00000-09-00-0696
B00000-09-00-0697
B00000-09-00-0698
B00000-09-00-0699 | Ice Management Controls Panel | COMPLETE |  | MACHINE SHOP

## Solenoid Signal I.D.'s
ID | Location | Type | 4-20 mA IN | Voltage IN | Digital IN (Sinking) | Digital IN (Sourcing) | 4-20 mA OUT | Voltage OUT | Relay OUT | 4-20mA OUT | Cryocon/LakeShore (NBX) | Serial Connection (NBX) | Pressure Indicator | # of Cables | # wires | Notes | Signal Type | INTERNAL Wiring Map Complete | EXTERNAL Wiring Map Complete | Cable Map (Definition) Complete | Schematic Diagram Complete
TEMPERATURE (CERNOX)
ID | Location | Type | [12 empty] | # wires | Notes
TR8611 | Cooldown Helium Supply Temp | Temperature (Cernox) | [8 empty] | 1 |  |  |  |  | +redundant | Cryocon/Ethernet
TR8622A | Lead A Top | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8622B | Lead B Top | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8624A | Lead A Bottom | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8624B | Lead B Bottom | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8670 | Lhe Tank Vent (pre-valve) | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8671 | Magnet Reservoir Return | Temperature (Cernox) | [8 empty] | 1 |  |  |  |  | +redundant | Cryocon/Ethernet
TR8672 | Shield Supply | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8673 | Shield Vent | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8674 | Lhe Tank Vent | Temperature (Cernox) | [8 empty] | 1 |  |  | 1 | 8 | +redundant | Cryocon/Ethernet
TR8610 |  | Temperature (Cernox) | [8 empty] | 1 |  |  | 1 | 8 | +redundant | Cryocon/Ethernet
TEMPERATURE (PT100)
ID | Location | Type | [12 empty] | # wires | Notes
TP8621A | Lead A Warm End | PT100 | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TP8621B | Lead B Warm End | PT100 | [8 empty] | 1 |  |  | 1 | 8 | +redundant | Cryocon/Ethernet
TP8675 | LHE Return Line Temp (outside can) | PT100 | [8 empty] | 1
TP8676A | LHE Return Line Temp (outside can) | PT100 | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TP8676B | LHE Return Line Temp (outside can) | PT100 | [8 empty] | 1
TP8677 | LHE Return Line (after pumps) | PT100 | [8 empty] | 1 |  |  | 1 | 8 | +redundant | Cryocon/Ethernet
PRESSURE
ID | Location | Type | [12 empty] | # wires | Notes
PT8620 | Lead Reservoir Pressure | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
PT8670 | Magnet Reservoir Pressure | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
PT8675A | LHE Return Line Press | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
PT8675B | LHE Return Line Press Sub-ATM | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
PT8677 | Inlet to guard vacuum | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
LL8620DP | Lead Reservoir dP LL | dP | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
LL8670DP | Magnet Reservoir dP LL | dP | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
TC8600 | Vacuum | Vacuum TC |  | 1 | [9 empty] | 1 | 2
LIQUID LEVEL
ID | Location | Type | [12 empty] | # wires | Notes
LL8620SC | Lead Reservoir LL | Superconducting Probe |  | 1 | [9 empty] | 1 |  |  | 0-10V
LL8670SC | Magnet Reservoir LL | Superconducting Probe |  | 1 | [9 empty] | 1 |  |  | 0-10V
VALVES
ID | Location | Type | [12 empty] | # wires | Notes | [5 empty] | Added
EV8611CD | Cooldown Bottom Fill | EV | [6 empty] | 2 |  |  |  |  | 2 | 2 | 2 x relay out | 24 VDC
EV8670BY | Lhe Return Valve | EV | [6 empty] | 2 |  |  |  |  | 2 |  | 2 x relay out | 24 VDC
EV8611JT | Top Fill | EV | [6 empty] | 2 |  |  |  |  | 2 | 2 | 2 x relay out | 24 VDC
EV8612 | Bottom Fill | EV | [6 empty] | 2 |  |  |  |  | 2 | 5 | 2 x relay out | 24 VDC
EV8611CD_LVDT | Cooldown Bottom Fill | EV | 1 | [10 empty] | 2 | 2 | LVDT analog in | 4-20 mA
EV8670BY_LVDT | Lhe Return Valve | EV | 1 | [10 empty] | 2 |  | LVDT analog in | 4-20 mA
EV8611JT_LVDT | Top Fill | EV | 1 | [10 empty] | 2 | 2 | LVDT analog in | 4-20 mA
EV8612_LVDT | Bottom Fill | EV | 1 | [10 empty] | 2 | 5 | LVDT analog in | 4-20 mA
PV8674 | Warm Return Valve | PV | [6 empty] | 1 | [6 empty] | Pnumatic Sealed Bellows | 4-20 mA
SV8622 | Lead Flow Vent to Atmosphere | Solenoid | [6 empty] | 1
SV8678CR | Warm Return Valve | Solenoid | [6 empty] | 1
SV8678DV | Warm Return Vent to Atmosphere | Solenoid | [6 empty] | 1
FI/EV 8621A | Lead A Flow Control | Analog in/out | 1 |  |  |  | 1 | [6 empty] | 1
FI/EV 8621B | Lead B Flow Control | Analog in/out | 1 |  |  |  | 1 | [6 empty] | 1
PV8600 | Vacuum Gate Valve | Solenoid Valve |  |  | 1 | [10 empty] | Digital input | 0-24 V
SV8675BY | Return Flow to Quench header | Solenoid Valve | [6 empty] | 1
HEATER
ID | Location | Type | [12 empty] | # wires | Notes
HT8621A | Lead A flag heater | Heater |  |  |  |  | 1 |  | 1
HT8621B | Lead B flag heater | Heater |  |  |  |  | 1 |  | 1
HTR8620 | Lead Reservoir (2 x 20 W) | Heater |  |  | 1 |  | 1 |  | 1 |  |  |  |  | 2 |  |  | Relay Out, Analogs Out, Digital IN
HTR8672 | Mag Reservoir Return (3 x 20 W) | Heater |  |  | 1 |  | 1 |  | 1 |  |  |  |  | 2 |  |  | Relay Out, Analogs Out, Digital IN
PRESSURE INDICATOR
ID | Location | Type | [12 empty] | # wires | Notes
PIXXXXX | Relief Valve Vacuum | ???? | [10 empty] | 1 |  |  | See zone G4 near guard vac
SYSTEM HEALTH
ID | Location | Type | [12 empty] | # wires | Notes
| 24 VDC OK | Digital |  |  | 3 | [8 empty] | 1 | 2 | internal wiring | Discrete IN
| UPS Low Power | Digital |  |  | 1 | [8 empty] | 1 | 2 | internal wiring | Discrete IN
| UPS on Battery | Digital |  |  | 1 | [8 empty] | 1 | 2 | internal wiring | Discrete IN
| Vacuum pump 1 speed | Analog |  | 1
| Vacuum pump 2 speed | Analog |  | 1
| Vacuum pump 1 ON | Digital | [6 empty] | 1
| Vacuum pump 2 ON | Digital | [6 empty] | 1
Magnet Monitoring/Control
ID | Location | Type | [12 empty] | # wires | Notes
| Fast Dump | Digital | [6 empty] | 1 | [5 empty] | 2 | internal wiring | Discrete IN
| Slow Dump | Digital | [6 empty] | 1 | [5 empty] | 2 | internal wiring | Discrete IN
| Power Supply Communications | Digital | [9 empty] | 1 |  |  | 2 | internal wiring | Discrete IN
| Quench Detector Status | Digital |  |  |  | 12
| Quench Detector Reset | Digital | [6 empty] | 1
| Power Supply Resets | Digital | [6 empty] | 3
| Watchdog/Keep Alive + Reset | Digital | [6 empty] | 2
| Power Supply Status | Digital |  |  | 6 | [9 empty] | 2 | internal wiring | Discrete IN
VFD's
ID | Location | Type | [12 empty] | # wires | Notes
MP8676A | Helium vacuum pallet | Mix | 1 |  | 1 |  | 1 |  | 1 | [6 empty] | Guess? | Mixed
MP8676B | Helium vacuum pallet | Mix | 1 |  | 1 |  | 1 |  | 1 |  |  |  |  | 1 | 2 | Guess? | Mixed
Vacuun Signals
ID | Location | Type | [19 empty] | Added
CG8606 | Mid level SST Vaccum gauge |  |  | 1 | [9 empty] | 40 |  | Analog Input | 0 -10V
CG8600TB | Extension on Turbo pump side |  |  | 1 | [11 empty] | Analog Input | 0 -10V
TB8600 (TURBO) | Speed Turbo Pump Vaccum at SST |  |  | 1 | [11 empty] | Analog Input | 0 -10V
|  | TOTALS | 15 | 8 | 16 | 12 | 8 | 0 | 29 | 0 | 9 | 1 | 1
IO Required
|  | Analog IN Channels (current) | 15
|  | Analog IN Channels (voltage) | 8
|  | Analog OUT Channels | 8
|  | Relay OUT Channels | 29
|  | Digital IN Channels (Sink) | 16
|  | Digital IN Channels (Source) | 12
|  | Cryocon/LakeShore | 9
|  | Enet NBX | 1
|  | Enet RS232 | 1
|  | PLC Equip Required |  |  | Spare Channels
|  | Analog Output | 2 |  | 8 | [10 empty] | TBNH | 2
|  | Analog Input (current in) | 2 |  | 17 | [10 empty] | TBCH | 9
|  | Analog Input (voltage in) | 1 |  | 8
|  | Relay Output | 3 |  | 19
|  | Digital Input (Sinking) | 1 |  | 16
|  | Digital Input (Sourcing) | 1 |  | 20
|  | SOE Module | 1
|  | L73 Processor | 1
|  | Ethernet Module | 2 |  |  |  |  | **this becomes 2 w/ remote chassis
|  | EWEB Module | 1
|  | Total Modules | 15
|  | PLC chassis (10 slot) | 2
|  | PLC Power Supply | 2
|  | Slot Filler | 5

## Solenoid Slow Controls
SOLENOID
| Summary | 2015-10-23
Rack Hardware & Infrastructure
| PLC Hardware | 25371.56
| Valve Control/Readback | 5396
| Temperature Monitoring | 5890
| Liquid Level | 4670
| Ethernet Communications | 5000
| Local HMI | 1290
| Rack Infrastructure | 9907.2
| External Cables | 15000
| Heater Control | 4551.38
| PLC Communications | 715
| Total Solenoid SLOW Controls Hardware | 77076.14
No. | Item | Mfg | PN | Qty | Vendor | Quote Unit Price | Total Est. Price | Date Ordered | Date Expected | PR# | Total Acutal Price | Location | NOTES:
PLC Hardware
1 | 10-Slot Chassis | Allen Bradley | 1756-A10 | 2 | EECO | 478.04 | 956.08
2 | Power Supply | Allen Bradley | 1756-PA72 | 2 | EECO | 708.18 | 1416.36
3 | PLC | Allen Bradley | 1756-L72 | 1 | EECO | 5964.4 | 5964.4
4 | Ethernet Module | Allen Bradley | 1756-EN2T | 2 | EECO | 2123.8 | 4247.6
5 | Ethernet Gateway | Allen Bradley | 1756-EWEB | 1 | EECO | 2331 | 2331 | [5 empty] | May not be necessary
6 | Digital Relay Output Module (16 Ch) | Allen Bradley | 1756-OW16I | 3 | EECO | 485.44 | 1456.32
7 | Analog Input Module (16 Ch.) | Allen Bradley | 1756-IF16 | 3 | EECO | 1206.2 | 3618.6
8 | Digital Input Module, 24 VDC Sink | Allen Bradley | 1756-IB32 | 1 | EECO | 396.26 | 396.26 | [5 empty] | Estimated Price
9 | Digital Input Module, 24 VDC Source | Allen Bradley | 1756-IV32 | 1 | EECO | 396.26 | 396.26 | [5 empty] | Estimated Price
10 | Sequence of Events Module | Allen Bradley | 1756-IB16ISOE | 1 | EECO | 664.52 | 664.52
11 | Analog Output Module (8 ch) | Allen Bradley | 1756-OF8 | 2 | EECO | 1554 | 3108
12 | Module Terminal Block (16 ch) | Allen Bradley | 1756-TBCH | 9 | EECO | 65.12 | 586.08
13 | Module Terminal Block (8 ch) | Allen Bradley | 1756-TBNH | 2 | EECO | 52.54 | 105.08
14 | Slot Filler | Allen Bradley | 1756-N2 | 5 | EECO | 25 | 125 | [5 empty] | Estimated Price
[5 empty] | PLC SUBTOTAL |  | 25371.56
Valve Actuation
15 | LVDT Excitation/Readback | Macro Sensors | LVC-2500 | 4 | Macro Sensors | 571 | 2284 | [6 empty] | x
16 | Relay | Finder | 44.62.7.024.4000 | 8 |  | 3 | 24 | [5 empty] | Price guess | x
17 | Relay Base | Finder | 95.75 | 8 |  | 3 | 24 | [5 empty] | Price guess | x
18 | Relay Diode | Finder | 99.01 | 8 |  | 8 | 64 | [5 empty] | Price guess | x
19 | Mass Flow Controller Head Unit | Teledyne Hastings | Power400 | 0 |  | 2000 | 0 | [5 empty] | Price guess
20 | Mass Flow Controller | Teledyne Hastings |  | 2 |  | 1500 | 3000 | [5 empty] | Price guess
[5 empty] | VALVE SUBTOTAL |  | 5396
Temperature Monitoring
21 | TCP to Ethernet/IP | Real Time Automation | 490-NBX | 1 | Real Time Automation | 715 | 715 | [5 empty] | Could also be 460ETCTCP (does parsing), same price | x
22 | CryoCon Temperature Monitor (8 ch) | CryoCon | 18C | 3 | CryoCon | 1695 | 5085 | [6 empty] | x
23 | CryoCon Panel Mount Kit | CryoCon | 3014-020 | 3 | CryoCon | 30 | 90 | [6 empty] | x
[5 empty] | TEMPERATURE SUBTOTAL |  | 5890
Liquid Level
52 | AMI Liquid Level Monitor | AMI |  | 2 | AMI | 835 | 1670
53 | AMI Liquid Level Probe | AMI |  | 2 | AMI | 1500 | 3000
[5 empty] | LIQUID LEVEL SUBTOTAL |  | 4670
Ethernet Communications
1 | Ethernet Switch | Cisco |  | 1 |  | 5000 | 5000 | [5 empty] | Based on Hall D's Ethernet Switch
[5 empty] | ETHERNET SUBTOTAL |  | 5000
Local HMI
1 | 10" Touch Panel (Local Control Panel) | Automation Direct | EA9-T10CL | 1 | Automation Direct | 1290 | 1290 | [6 empty] | x
[5 empty] | HMI SUBTOTAL |  | 1290
Rack Infrastructure
1 | Rack | - | - | 2 | 0 | 0 | 0 | N/A |  | N/A |  | Hall B | Already on hand
2 | Back Panel |  |  | 3 |  | 200 | 600 | [6 empty] | x
22 | 24 VDC Power Supply | RHINO | PSM24-360S | 4 | Automation Direct | 229 | 916 | [6 empty] | x
23 | 24VDC Redundancy Module | RHINO | PSM24-REM360S | 2 | Automation Direct | 159 | 318 | [6 empty] | x
24 | 15 Amp Circuit Breaker | Allen Bradley | 1492-CB1G150 | 2 | EECO | 43.99 | 87.98 | [6 empty] | x
25 | 5 Amp Circuit Breaker | Allen Bradley | 1492-CB1G050 | 18 | EECO | 46.08 | 829.44 | [6 empty] | x
26 | 2 Amp Circuit Breaker | Allen Bradley | 1489-M1C020 | 4 | EECO | 53 | 212 | [6 empty] | x
27 | Terminal block single level | Allen Bradley | 1492-J3 | 40 | EECO | 1.11 | 44.4 | [6 empty] | x
28 | Grounding Block | Allen Bradley | 1492-JG3 | 50 | EECO | 5.51 | 275.5 | [6 empty] | x
29 | End Barrier for J3 | Allen Bradley | 1492-EBJ3 | 4 | EECO | 0.83 | 3.32 | [6 empty] | x
30 | End Anchor for J3 | Allen Bradley | 1492-EAHJ35 | 25 | EECO | 4.37 | 109.25 | [6 empty] | x
31 | Terminal group marker | Allen Bradley | 1492-G35 | 26 | EECO | 3.99 | 103.74 | [6 empty] | x
35 | 10 Screw Center Jumper | Allen Bradley | 1492-CJJ5-10 | 10 | EECO | 5 | 50 | [5 empty] | price guess | x
37 | Terminal block 3 level | Allen Bradley | 1492-WTF3 | 160 | EECO | 8.39 | 1342.4 | [6 empty] | x
38 | End Barrier for WTF3 | Allen Bradley | 1492-EBTF3 | 10 | EECO | 1.74 | 17.4 | [6 empty] | x
39 | End Anchor for WTF3 | Allen Bradley | 1492-EAJ35 | 10 | EECO | 2.05 | 20.5 | [6 empty] | x
40 | 3 level + ground | Allen Bradley | 1492-JT3M | 77 | EECO | 5.4 | 415.8 | [6 empty] | x
41 | End Barrier for JT3M | Allen Bradley | 1492-EBJ3TM | 5 | EECO | 1.42 | 7.1 | [6 empty] | x
42 | Jumpers, 20 pole Red | Allen Bradley | 1492-SJT5-20-R | 10 | EECO | 9.32 | 93.2 | [6 empty] | x
43 | Jumpers, 20 pole Blue | Allen Bradley | 1492-SJT5-20-B | 10 | EECO | 9.32 | 93.2 | [6 empty] | x
44 | DIN Rail | Allen Bradley | 199-DR1 | 6 | EECO | 10.83 | 64.98 | [6 empty] | x
45 | Wire Duct | Panduit | 2X4LG6, C2X4LG6 | 120 | VAROIUS | 10 | 1200 | [6 empty] | x
49 | UPS | APC | SMX2000RMLV2U | 1 | Newegg | 1159.99 | 1159.99 | [6 empty] | x
50 | Relay Smartcard for UPS | APC | AP9613 | 1 | TigerDirect | 200 | 200 | [6 empty] | x
51 | Vertical Power Strip | Hammond | 1587T10A1 | 0 | Allied Electronics | 84.62 | 0
30 | Hookup Wire |  |  | 1500 |  | 1 | 1500 | [5 empty] | 800' @ $1/foot..
54 | Timer Relay (for watchdog) | Tyco | CNT-35-96 | 1 |  | 225 | 225 | [6 empty] | x
55 | Control Relay 3PDT | Allen Bradley | 700HA33Z24 | 1 |  | 18 | 18 | [6 empty] | x
55 | Relay for SOE (relay + base) | Finder | 44.62.7.024.4000 | 18 |  | 14 | 252 | [6 empty] | x
[5 empty] | INFRASTRUCTURE SUBTOTAL |  | 9907.2
External Cables (Between Racks & Can)
1 | Generic Cables |  |  | 30 |  | 500 | 15000 | [5 empty] | Estimated price per cable (if build by contractor)
[5 empty] | EXTERNAL CABLING SUBTOTAL |  | 15000
Heater Control Box
1 | Enclosure | Hoffman? |  | 2 |  | 100 | 200
2 | Backpanel | Hoffman? |  | 2 |  | 100 | 200
3 | Solid State Relay |  |  | 2 |  | 50 | 100
4 | Interposing Relay + Base | Finder | Same as EV's | 4 |  | 60 | 240
5 | Din Rail | Allen Bradley | 199-DR1 | 2 |  | 10.83 | 21.66
6 | Terminal block single level | Allen Bradley | 1492-J3 | 20 | EECO | 1.11 | 22.2
7 | Grounding Block | Allen Bradley | 1492-JG3 | 4 | EECO | 5.51 | 22.04
8 | End Barrier for J3 | Allen Bradley | 1492-EBJ3 | 4 | EECO | 0.83 | 3.32
9 | End Anchor for J3 | Allen Bradley | 1492-EAHJ35 | 6 | EECO | 4.37 | 26.22
10 | Terminal group marker | Allen Bradley | 1492-G35 | 4 | EECO | 3.99 | 15.96
11 | Hookup Wire |  |  | 60 |  | 1 | 60 | [5 empty] | 60' @ $1/foot…
12 | Heaters (Immersion) | Chromalox |  | 2 |  | 100 | 200
13 | Feedthrough | Kurt J Lesker |  | 2 |  | 250 | 500
14 | Vacuum Connector | Kurt J Lesker |  | 2 |  | 125 | 250
15 | Air Side Connector | Kurt J Lesker |  | 2 |  | 125 | 250
16 | LHe Reservoir Heaters | AMTEK | DLM60-10M13M51A | 2 |  | 1159.99 | 2319.98
17 | Rack Mount Hardware kit | AMTEK | DLMRK | 2 |  | 60 | 120
18 |  |  |  | 2
[5 empty] | HEATER CONTROLS SUBTOTAL |  | 4551.38
Power Supply Communications
18 | RS232 to Ethernet/IP | Real Time Automation | 435-NBX | 1 | Real Time Automation | 715 | 715 | [6 empty] | x
|  |  |  | PLC COMMUNICATIONS SUBTOTAL |  |  | 715

## TB's
| Analog Output | Analog Input (Current) | Analog Input (Voltage) | Digital Output - Relay | Digital Input - Sinking | Digital Input - Sourcing | Digital Input - SOE | 24 VDC (10 circuit)
1492-J3 | [7 empty] | 19
1492-EBJ3 | [7 empty] | 2
1492-JT3M | 10 | 19 | 19
1492-EBJT3M | 1 | 1 | 1
1492-GM35 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2
1492-WTF3 |  |  |  | 16 |  | 33 | 16
1492-EBTF3 |  |  |  | 1 |  | 1 | 1
1492-JD3 |  |  |  |  | 33
1492-EBJD3 |  |  |  |  | 1

## Solenoid PLC Channel Layout
Power Supply
2017-02-02 |  |  |  |  | HALL B SOLENOID | [6 empty] | PLC (processor)
[5 empty] | LOCAL PLC 0: I / O CHANNEL LOCATIONS | [6 empty] | Communication
NOT USED
Chassis 0: | Slot 0 | PLC Channels | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 | Slot 9 | UNDIFINED
1756-PA72 | 1756-L72 | LOCAL | 1756-OF8 | 1756-OF8 | 1756-N2 | 1756-IF16 | 1756-IF16 | 1756-IF16 | 1756-N2 | 1756-EWEB | 1756-EN2T | SLOT FILLER
|  | Bit/Channel 00 | Slot 1: PV8674; Slot 2: FV8621A_OUT; Slot 4: PT8620 4K He LEAD RESERVOIR; Slot 5: HTR8620 VOLTAGE_IN; Slot 6: TC8600 VAC THERMOCOUPLE | REMOVED
|  | Bit/Channel 01 | Slot 2: FV8621B_OUT; Slot 4: PT8670 4K He MAGNET RESVR.; Slot 5: HTR8620 CURRENT_IN; Slot 6: LL8620SC LHe LEVEL | ADDED
|  | Bit/Channel 02 | Slot 2: HTR8620 VOLTAGE_OUT; Slot 4: PT8675A; Slot 5: HTR8672 VOLTAGE_IN; Slot 6: LL8670SC LHe LEVEL
|  | Bit/Channel 03 | Slot 2: HTR8620 CURRENT_OUT; Slot 4: PT86XX SPARE; Slot 5: HTR8672 CURRENT_IN
|  | Bit/Channel 04 | Slot 2: HTR8672 VOLTAGE_OUT; Slot 4: PT8677 GUARD INLET; Slot 6: CG8606 VACUUM
|  | Bit/Channel 05 | Slot 2: HTR8672 CURRENT_OUT; Slot 4: LL8620DP Lhe LEAD RESVR. DP; Slot 6: CG8600TB VACUUM
|  | Bit/Channel 06 | Slot 2: HALL SENSOR CURRENT_OUT; Slot 4: LL8670DP Lhe MAG. RESVR. DP; Slot 6: TB8600 (TURBO SPEED)
|  | Bit/Channel 07 | Slot 4: PT86XX SPARE
|  | Bit/Channel 08 | Slot 4: PT86XX SPARE
Bit/Channel 09 | bar: Slot 7 to Slot 8
|  | Bit/Channel 10 | Slot 5: FI8621A LEAD A FLOW_CONTROL
|  | Bit/Channel 11 | Slot 5: FI8621B LEAD B FLOW_CONTROL
|  | Bit/Channel 12 | Slot 5: EV8611CD _LVDT
|  | Bit/Channel 13 | Slot 5: EV8670BY _LVDT
|  | Bit/Channel 14 | Slot 5: EV8611JT _LVDT
|  | Bit/Channel 15 | Slot 5: EV8612 _LVDT
|  |  | DWG No. -0623 Rev - | DWG No. -0624 Rev - |  | DWG No. -0626 Rev - | DWG No. -0627 Rev - | DWG No. -0628 Rev -
Power Supply
2017-01-25 |  |  | Slot 3: HALL B SOLENOID | PLC (processor)
|  |  | Slot 3: SOLENOID REMOTE PLC 1: I / O CHANNEL LOCATIONS | Communication
NOT USED
Chassis 1: | PLC Channels | Slot 0 | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 | Slot 9 | UNDIFINED
1756-PA72 | LOCAL | 1756-OW16I | 1756-OW16I | 1756-OW16I | 1756-N2 | 1756-IB32 | 1756-IV32 | 1756-IV32 | 1756-IB16ISOE | 1756-N2 | 1756EN2T | SLOT FILLER
| Bit/Channel 00 | EV8611CD_OPEN | KEEP_ALIVE_RESET | SV8622_OPEN |  | HTR8620 _READBACK | QD1_CH1_L1 | QD3_CH1_L1 | LEAD TEMPERATURE |  |  | REMOVED
| Bit/Channel 01 | EV8611CD_CLOSE |  | SV8678CR_OPEN |  | HTR8672 _READBACK | QD1_CH1_U1 | QD3_CH1_U1 | Lhe LIQUID LEVEL_8620SC |  |  | ADDED
| Bit/Channel 02 | EV8670BY_OPEN |  | SV8678DV_OPEN |  | 24VDC_BAD _LOCAL | QD1_CH2_L2 | QD3_CH2_L2 | Lhe LIQUID LEVEL_8670SC
| Bit/Channel 03 | Slot 0: EV8670BY_CLOSE; Slot 4: UPS_LOW; Slot 5: QD1_CH2_U2; Slot 6: QD3_CH2_U2; Slot 7: CRYOCONS RELAY 1
| Bit/Channel 04 | Slot 0: EV8611JT_OPEN; Slot 4: UPS_ON_BATT; Slot 5: QD1_CH3_L3; Slot 6: QD3_CH3_L3; Slot 7: CRYOCONS RELAY 2
| Bit/Channel 05 | Slot 0: EV8611JT_CLOSE; Slot 4: 24VDC_BAD _REMOTE; Slot 5: QD1_CH3_U3; Slot 6: QD3_CH3_U3
| Bit/Channel 06 | Slot 0: EV8612_OPEN; Slot 4: PV8600TB VAC; Slot 5: QD1_CH4_L4; Slot 6: QD3_CH4_L4; Slot 7: PLC_FAST_DUMP
| Bit/Channel 07 | Slot 0: EV8612_CLOSE; Slot 5: QD1_CH4_U4; Slot 6: QD3_CH4_U4; Slot 7: VACUUM SUM INTERLOCK
| Bit/Channel 08 | Slot 0: HTR8620 EXTERNAL-OFF; Slot 7: WATCHDOG
| Bit/Channel 09 | Slot 0: HTR8620 ENABLE_ON
| Bit/Channel 10 | Slot 0: HTR8672 EXTERNAL-OFF; Slot 1: H. S. CURRENT SOURCE POLARITY; Slot 7: VT_CABLE_ INTLCK
| Bit/Channel 11 | Slot 0: HTR8672 ENABLE_ON; Slot 1: PLC_FAST_DUMP; Slot 5: PSU_480V_ON; Slot 7: SYSTEM_CABLE _INTERLOCK
| Bit/Channel 12 | Slot 1: PLC_FAST_DUMP _BACKUP; Slot 5: PSU_MAIN _POWER; Slot 7: FAST QD1 _INTERLOCK
| Bit/Channel 13 | Slot 1: PLC_SLOW_DUMP; Slot 5: PSU_SUM _INTERLOCKS; Slot 7: FAST QD2 _INTERLOCK
| Bit/Channel 14 | Slot 0: HTR8621_A SSR1_ON; Slot 1: KEEP_ALIVE _CONTROL; Slot 5: PSU_READY; Slot 7: FAST QD3 _INTERLOCK
| Bit/Channel 15 | Slot 0: HTR8621_B SSR2_ON; Slot 1: MPS_CPU_RESET; Slot 2: PV8600_OPEN; Slot 5: DUMP_SWITCH _STATUS; Slot 7: FAST QD4 _INTERLOCK
| Bit/Channel 16 | Slot 5: QD2_CH1_L1; Slot 6: QD4_CH1_L1
| Bit/Channel 17 | Slot 5: QD2_CH1_U1; Slot 6: QD4_CH1_U1
| Bit/Channel 18 | Slot 5: QD2_CH2_L2; Slot 6: QD4_CH2_L2 |  | 0
| Bit/Channel 19 | Slot 5: QD2_CH2_U2; Slot 6: QD4_CH2_U2
| Bit/Channel 20 | Slot 5: QD2_CH3_L3; Slot 6: QD4_CH3_L3
| Bit/Channel 21 | Slot 5: QD2_CH3_U3; Slot 6: QD4_CH3_U3
| Bit/Channel 22 | Slot 5: QD2_CH4_L4; Slot 6: QD4_CH4_L4
| Bit/Channel 23 | Slot 5: QD2_CH4_U4; Slot 6: QD4_CH4_U4
Bit/Channel 24 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 25 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 26 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 27 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 28 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 29 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 30 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 31 | bar: Slot 0 to Slot 2; Slot 7
|  | DWG No. -0638 Rev - | DWG No. -0639 Rev - | DWG No. -0640 Rev - |  | DWG No. -0641 Rev - | DWG No. -0642 Rev - | DWG No. -0643 Rev - | DWG No. -0645 Rev -

## LV Chassis Layout
2016-10-26
Solenoid Chassis Layout -- view is looking at the back of the chassis
CHASSIS 1
| TR |  |  | PT |  |  |  | LC
| J1 |  | J5 | J9 | J13 | J17 | J21 | J25 |  | Spares Chassis 1
| J2 |  | J6 | J10 | J14 | J18 | J22 | J26 |  | 8
| J3 |  | J7 | J11 | J15 | J19 | J23 | J27
| J4 |  | J8 | J12 | J16 | J20 | J24 | J28
CHASSIS 2
| TR |  |  | PT |  | HS |  | LC
| J1 |  | J5 | J9 | J13 | J17 | J21 | J25 |  | Spares Chassis2
| J2 |  | J6 | J10 | J14 | J18 | J22 | J26 |  | 16
| J3 |  | J7 | J11 | J15 | J19 | J23 | J27
| J4 |  | J8 | J12 | J16 | J20 | J24 | J28
Each connector has 2 channels (A, B) - cryocon pinout
LC channel can also be HS channel. Excitation is the same
|  |  | PLC Arrays | [14 empty] | CHANGE THIS DATA TO ADJUST THE DEFAULT VALUES FOR THE SENSOR TYPES!
|  |  | Name | Size* | *element 0 of each array is a counter -- | [13 empty] | Excitation | AC/DC | Excitation | Calibration | PLC Units
|  |  | LC_From_Sol_cRIO | 16 | cRIO to increment by 1 each time the array is updated -- roll over to 0 at 2^31 | [12 empty] | TR | I | AC | .3-10 | LOOKUP | K
|  |  | SG_From_Sol_cRIO | 0 | [13 empty] | SG | V | DC | 5 | FORMULA | nV/V
|  |  | PT_From_Sol_cRIO | 15 | [13 empty] | TP | I | DC | 2.5 | LOOKUP | K
|  |  | TR_From_Sol_cRIO | 26 | [13 empty] | LC | V | DC | 5 | LOOKUP | lb
|  |  | HS_From_Sol_cRIO | 1 | [13 empty] | HS | V | DC | 2.5 | LOOKUP | G
[18 empty] | ELSE | ????? | ????? | ????? | ????? | ?????
Dwg. # | Name from Vendor | Jlab PV Name | Chassis | Connector | Channel | Type (TR, SG,…) | Serial # | Location/Description | Excitation | AC/DC | Excitation (uA or V) | Calibrated? | Read Register Address | Write Register Address | Calib. Type | PLC Tag (DINT) | PLC Tag Type | PLC Units | Notes
-0665 | TS01 | TR86101CP_B | 1 | J1 | A | TR | X100007 | Cooling Plate Lower TS 1 | LOOKUP | AC | 0.3 - 20 |  | 38 | 0 | LOOKUP | TR_From_Sol_cRIO[1] | DINT | K
-0665 | TS02 | TR86102CP_B | 1 | J1 | B | TR | X99799 | Cooling Plate Lower TS 2 | LOOKUP | AC | 0.3 - 20 |  | 39 | 1 | LOOKUP | TR_From_Sol_cRIO[2] | DINT | K
-0665 | TS03 | TR86103CP_T | 1 | J2 | A | TR | X99776 | Cooling Plate Upper TS 1 | LOOKUP | AC | 0.3 - 20 |  | 3a | 2 | LOOKUP | TR_From_Sol_cRIO[3] | DINT | K
-0665 | TS04 | TR86104CP_T | 1 | J2 | B | TR | X99801 | Cooling Plate Upper TS 2 | LOOKUP | AC | 0.3 - 20 |  | 3b | 3 | LOOKUP | TR_From_Sol_cRIO[4] | DINT | K
-0665 | TS05 | TR86105C1 | 1 | J3 | A | TR | X99453 | Coil 1 ID Upper TS 1 | LOOKUP | AC | 0.3 - 20 |  | 3c | 4 | LOOKUP | TR_From_Sol_cRIO[5] | DINT | K
-0665 | TS06 | TR86106C1 | 1 | J3 | B | TR | X101015 | Coil 1 ID Upper TS 2 | LOOKUP | AC | 0.3 - 20 |  | 3d | 5 | LOOKUP | TR_From_Sol_cRIO[6] | DINT | K
-0665 | TS07 | TR86107C2 | 1 | J4 | A | TR | X100862 | Coil 2 ID Upper TS 1 | LOOKUP | AC | 0.3 - 20 |  | 3e | 6 | LOOKUP | TR_From_Sol_cRIO[7] | DINT | K
-0665 | TS08 | TR86108C2 | 1 | J4 | B | TR | X99452 | Coil 2 ID Upper TS 2 | LOOKUP | AC | 0.3 - 20 |  | 3f | 7 | LOOKUP | TR_From_Sol_cRIO[8] | DINT | K
-0665 | TS09 | TR86109C3 | 1 | J5 | A | TR | X101013 | Coil 3 OD Upper TS 1 | LOOKUP | AC | 0.3 - 20 |  | 40 | 8 | LOOKUP | TR_From_Sol_cRIO[9] | DINT | K
-0666 | TS10 | TR86110C3 | 2 | J2 | A | TR | X109494 | Coil 3 OD Upper TS 2 | LOOKUP | AC | 0.3 - 20 |  | 3a | 2 | LOOKUP | TR_From_Sol_cRIO[10] | DINT | K
-0667 | TS11 | TR86111C4 | 2 | J3 | A | TR | X110279 | Coil 4 OD Upper TS1 | LOOKUP | AC | 0.3 - 20 |  | 3c | 4 | LOOKUP | TR_From_Sol_cRIO[11] | DINT | K
-0667 | TS12 | TR86112C4 | 2 | J3 | B | TR | X109520 | Coil 4 OD Upper TS2 | LOOKUP | AC | 0.3 - 20 |  | 3d | 5 | LOOKUP | TR_From_Sol_cRIO[12] | DINT | K
-0667 | TS13 | TR86113C5 | 2 | J4 | A | TR | X109493 | Coil 5 OD Upper TS 1 | LOOKUP | AC | 0.3 - 20 |  | 3e | 6 | LOOKUP | TR_From_Sol_cRIO[13] | DINT | K
-0667 | TS14 | TR86114C5 | 2 | J4 | B | TR | X110278 | Coil 5 OD Upper TS 2 | LOOKUP | AC | 0.3 - 20 |  | 3f | 7 | LOOKUP | TR_From_Sol_cRIO[14] | DINT | K
-0666 | TS15 | TR86115SP_C1_C3 | 1 | J6 | A | TR | X101016 | Splice 1 TS 1 | LOOKUP | AC | 0.3 - 20 |  | 42 | a | LOOKUP | TR_From_Sol_cRIO[15] | DINT | K
-0666 | TS16 | TR86116SP_C1_C3 | 1 | J6 | B | TR | X99428 | Splice 1 TS 2 | LOOKUP | AC | 0.3 - 20 |  | 43 | b | LOOKUP | TR_From_Sol_cRIO[16] | DINT | K
-0666 | TS17 | TR86117SP_C3_C5 | 1 | J7 | A | TR | X101014 | Splice 2 TS 1 | LOOKUP | AC | 0.3 - 20 |  | 44 | c | LOOKUP | TR_From_Sol_cRIO[17] | DINT | K
-0666 | TS18 | TR86118SP_C3_C5 | 1 | J7 | B | TR | X110276 | Splice 2 TS 2 | LOOKUP | AC | 0.3 - 20 |  | 45 | d | LOOKUP | TR_From_Sol_cRIO[18] | DINT | K
-0666 | TS19 | TR86119SP_C4_C5 | 1 | J8 | A | TR | X110277 | Splice 5 TS 1 | LOOKUP | AC | 0.3 - 20 |  | 46 | e | LOOKUP | TR_From_Sol_cRIO[19] | DINT | K
-0666 | TS20 | TR86120SP_C4_C5 | 1 | J8 | B | TR | X109521 | Splice 5 TS 2 | LOOKUP | AC | 0.3 - 20 |  | 47 | f | LOOKUP | TR_From_Sol_cRIO[20] | DINT | K
-0666 | TS21 | TR86121SP_C2_C4 | 2 | J1 | A | TR | X109519 | Splice 6 TS 1 | LOOKUP | AC | 0.3 - 20 |  | 38 | 0 | LOOKUP | TR_From_Sol_cRIO[21] | DINT | K
-0666 | TS22 | TR86122SP_C2_C4 | 2 | J1 | B | TR | X109522 | Splice 6, TS 2 | LOOKUP | AC | 0.3 - 20 |  | 39 | 1 | LOOKUP | TR_From_Sol_cRIO[22] | DINT | K
-0667 | TS23 | TR86123RS_US_T_BL_C | 2 | J5 | A | TR | X110290 | Suspension 5 CM TS | LOOKUP | AC | 0.3 - 20 |  | 40 | 8 | LOOKUP | TR_From_Sol_cRIO[23] | DINT | K
-0667 | TS24 | TR86124RS_DS_B_BL_C | 2 | J5 | B | TR | X110287 | Suspension 7 CM TS | LOOKUP | AC | 0.3 - 20 |  | 41 | 9 | LOOKUP | TR_From_Sol_cRIO[24] | DINT | K
-0667 | TS25 | TP86125RS_US_T_BL_M | 1 | J9 | A | TP | P31432 | Suspension 5 Midlink TS 1 | LOOKUP | DC | 2500 |  | 48 | 10 | LOOKUP | PT_From_Sol_cRIO[1] | DINT | K
-0667 | TS26 | TP86126RS_US_T_BL_M | 1 | J9 | B | TP | P31433 | Suspension 5 Midlink TS 2 | LOOKUP | DC | 2500 |  | 49 | 11 | LOOKUP | PT_From_Sol_cRIO[2] | DINT | K
-0667 | TS27 | TP86127RS_DS_B_BL_M | 1 | J10 | A | TP | P31444 | Suspension 7 Midlink TS | LOOKUP | DC | 2500 |  | 4a | 12 | LOOKUP | PT_From_Sol_cRIO[3] | DINT | K
-0668 | TS28 | TP86128HS_BO_B_BR | 1 | J11 | A | TP | P31491 | Rad Shield Bore Lower TS 1 | LOOKUP | DC | 2500 |  | 4b | 13 | LOOKUP | PT_From_Sol_cRIO[4] | DINT | K
-0668 | TS29 | TP86129HS_BO_B_BL | 1 | J11 | B | TP | P32302 | Rad Shield Bore Lower TS 2 | LOOKUP | DC | 2500 |  | 4c | 14 | LOOKUP | PT_From_Sol_cRIO[5] | DINT | K
-0668 | TS30 | TP86130HS_B_OD | 1 | J12 | A | TP | P32304 | Rad Shield OD Lower TS 1 | LOOKUP | DC | 2500 |  | 4d | 15 | LOOKUP | PT_From_Sol_cRIO[6] | DINT | K
-0668 | TS31 | TP86131HS_B_OD | 1 | J12 | B | TP | P32305 | Rad Shield OD Lower TS 2 | LOOKUP | DC | 2500 |  | 4e | 16 | LOOKUP | PT_From_Sol_cRIO[7] | DINT | K
-0668 | TS32 | TR86132BOB_US | 2 | J6 | A | TR | X110289 | C1-4 Bobbin TS 1 | LOOKUP | AC | 0.3 - 20 |  | 42 | a | LOOKUP | TR_From_Sol_cRIO[25] | DINT | K
-0668 | TS33 | TR86133BOB_DS | 2 | J6 | B | TR | X110288 | C1-4 Bobbin TS 2 | LOOKUP | AC | 0.3 - 20 |  | 43 | b | LOOKUP | TR_From_Sol_cRIO[26] | DINT | K
-0668 | TS34 | TP86134HS_US_CO_LBR | 1 | J13 | A | TP | P32306 | Rad Shield Cone TS 1 | LOOKUP | DC | 2500 |  | 4f | 17 | LOOKUP | PT_From_Sol_cRIO[8] | DINT | K
-0669 | TS35 | TP86135HS_DS_CO_XXX | 1 | J14 | A | TP | P32307 | Rad Shield Cone TS 2 | LOOKUP | DC | 2500 |  | 50 | 18 | LOOKUP | PT_From_Sol_cRIO[9] | DINT | K
-0669 | TS36 | TP86136HS_DS_CO_XXX | 1 | J14 | B | TP | P32308 | Rad Shield Cone TS 3 | LOOKUP | DC | 2500 |  | 51 | 19 | LOOKUP | PT_From_Sol_cRIO[10] | DINT | K
-0669 | TS37 | TP86137HS_US_CO_UBR | 1 | J15 | A | TP | P32310 | Rad Shield Cone TS 4 | LOOKUP | DC | 2500 |  | 52 | 1a | LOOKUP | PT_From_Sol_cRIO[11] | DINT | K
-0669 | TS38 | TP86138HS_US_CO_UBL | 1 | J15 | B | TP | P32311 | Rad Shield Cone TS 5 | LOOKUP | DC | 2500 |  | 53 | 1b | LOOKUP | PT_From_Sol_cRIO[12] | DINT | K
-0669 | TS39 | TP86139HS_DS_CO_UBL | 1 | J16 | A | TP | P32315 | Rad Shield Cone TS 6 | LOOKUP | DC | 2500 |  | 54 | 1c | LOOKUP | PT_From_Sol_cRIO[13] | DINT | K
-0669 | TS40 | TP86140HS_DS_CO_LBL | 1 | J16 | B | TP | P32314 | Rad Shield Cone TS 7 | LOOKUP | DC | 2500 |  | 55 | 1d | LOOKUP | PT_From_Sol_cRIO[14] | DINT | K
-0669 | TS41 | TP86141HS_US_CO_LBL | 2 | J9 | A | TP | P32316 | Rad Shield Cone TS 8 | LOOKUP | DC | 2500 |  | 48 | 10 | LOOKUP | PT_From_Sol_cRIO[15] | DINT | K
-0662-1 | RLC86701-RL07 | RS86107DS_BL_B | 1 | J25 | A | LC | 200610240 | Solenoid DS BL Radial Support Lower | LOOKUP | DC | 5 |  | 68 | 30 | LOOKUP | LC_From_Sol_cRIO[1] | DINT | lb
-0662-1 | ALC86701-AL07 | ZS86107DS_BL_B | 1 | J25 | B | LC | 310292 | Solenoid DS BL Axial Support Lower | LOOKUP | DC | 5 |  | 69 | 31 | LOOKUP | LC_From_Sol_cRIO[2] | DINT | lb
-0662-1 | RLC86704-RL06 | RS86106DS_BL_T | 1 | J26 | A | LC | 200610239 | Solenoid DS BL Radial Support Upper | LOOKUP | DC | 5 |  | 6a | 32 | LOOKUP | LC_From_Sol_cRIO[3] | DINT | lb
-0662-1 | ALC86704-AL06 | ZS86106DS_BL_T | 1 | J26 | B | LC | 310291 | Solenoid DS BL Axial Support Upper | LOOKUP | DC | 5 |  | 6b | 33 | LOOKUP | LC_From_Sol_cRIO[4] | DINT | lb
-0662-2 | RLC86705-RL03 | RS86103DS_BR_T | 1 | J27 | A | LC | 200610235 | Solenoid DS BR Radial Support Upper | LOOKUP | DC | 5 |  | 6c | 34 | LOOKUP | LC_From_Sol_cRIO[5] | DINT | lb
-0662-2 | ALC86705-AL03 | ZS86103DS_BR_T | 1 | J27 | B | LC | 310288 | Solenoid DS BR Axial Support Upper | LOOKUP | DC | 5 |  | 6d | 35 | LOOKUP | LC_From_Sol_cRIO[6] | DINT | lb
-0662-2 | RLC86708-RL02 | RS86102DS_BR_B | 1 | J28 | A | LC | 200610233 | Solenoid DS BR Radial Support Lower | LOOKUP | DC | 5 |  | 6e | 36 | LOOKUP | LC_From_Sol_cRIO[7] | DINT | lb
-0662-2 | ALC86708-AL02 | ZS86102DS_BR_B | 1 | J28 | B | LC | 310287 | Solenoid DS BR Axial Support Lower | LOOKUP | DC | 5 |  | 6f | 37 | LOOKUP | LC_From_Sol_cRIO[8] | DINT | lb
-0662-3 | RLC86703-RL05 | RS86105US_BL_T | 2 | J25 | A | LC | 200610237 | Solenoid US BL Radial Support Upper | LOOKUP | DC | 5 |  | 68 | 30 | LOOKUP | LC_From_Sol_cRIO[9] | DINT | lb
-0662-3 | ALC86703-AL05 | ZS86105US_BL_T | 2 | J25 | B | LC | 310290 | Solenoid US BL Axial Support Upper | LOOKUP | DC | 5 |  | 69 | 31 | LOOKUP | LC_From_Sol_cRIO[10] | DINT | lb
-0662-3 | RLC86702-RL08 | RS86108US_BL_B | 2 | J26 | A | LC | 201610067 | Solenoid US BL Radial Support Lower | LOOKUP | DC | 5 |  | 6a | 32 | LOOKUP | LC_From_Sol_cRIO[11] | DINT | lb
-0662-3 | ALC86702-AL08 | ZS86108US_BL_B | 2 | J26 | B | LC | 310293 | Solenoid US BL Axial Support Lower | LOOKUP | DC | 5 |  | 6b | 33 | LOOKUP | LC_From_Sol_cRIO[12] | DINT | lb
-0662-4 | RLC86706-RL04 | RS86104US_BR_T | 2 | J27 | A | LC | 200610236 | Solenoid US BR Radial Support Upper | LOOKUP | DC | 5 |  | 6c | 34 | LOOKUP | LC_From_Sol_cRIO[13] | DINT | lb
-0662-4 | ALC86706-AL04 | ZS86104US_BR_T | 2 | J27 | B | LC | 310289 | Solenoid US BR Axial Support Upper | LOOKUP | DC | 5 |  | 6d | 35 | LOOKUP | LC_From_Sol_cRIO[14] | DINT | lb
-0662-4 | RLC86707-RL01 | RS86101US_BR_B | 2 | J28 | A | LC | 200610232 | Solenoid US BR Radial Support Lower | LOOKUP | DC | 5 |  | 6e | 36 | LOOKUP | LC_From_Sol_cRIO[15] | DINT | lb
-0662-4 | ALC86707-AL01 | ZS86101US_BR_B | 2 | J28 | B | LC | 310277 | Solenoid US BR Axial Support Lower | LOOKUP | DC | 5 |  | 6f | 37 | LOOKUP | LC_From_Sol_cRIO[16] | DINT | lb
-0662-5 | HS1 | HS1 | 2 | J17 | A | HS |  | Solenoid DS end (0 deg) | LOOKUP | DC |  |  | 56 | 1e | LOOKUP | HS_From_Sol_cRIO[1] | DINT | G
-0662-5 | HS2 | HS2 | 2 | J18 | A | HS |  | Solenoid DS end (120 deg) | LOOKUP | DC |  |  | 58 | 20
-0662-6 | HS3 | HS3 | 2 | J18 | B | HS |  | Solenoid DS end (240 deg) | LOOKUP | DC |  |  | 59 | 21

## CRYOCON MAPS
2016-12-21
SOLENOID
CRYOCON MAPPING
CRYOCON 1 |  |  | CRYOCON 2 |  |  | CRYOCON 3
Channel | PV | Serial No. | Channel | PV | Serial No. | Channel | PV | Serial No.
A | TR8622A | X100355 | A | TR8670 | X103728 | A | TP8622A | WCL1
redundant | TR8622Ar | X100312 | redundant | TR8670r | X103236
B | TR8622B | X103646 | B | TR8673 | X103692 | B | TP8622Ar | WCL1
redundant | TR8622Br | X100394 | redundant | TR8673r | X103693
C | TR8611 | X103241 | C | TR8674 | X103739 | C | TP8622B | WCL2
redundant | TR8611r | X103326 | redundant | TR8674r | X103713
D | TR8672 | X103328 | D |  |  | D | TP8622Br | WCL2
redundant | TR8672r | X103689
E | TR8671 | X103690 | E | TR8624A | X103735 | E | TP8611
redundant | TR8671r | X103691 | SPARE |  |  | redundant | TP8611r
F |  |  | F | TR8624B | X103736 | F | TP8620A
redundant |  |  | SPARE |  |  | redundant | TP8620Ar
G | TR8610 | X111832 | G | TP8621A |  | G | TP8620B
|  |  | redundant | TP8621Ar |  | redundant | TP8620Br
H | TR8610r | X111864 | H | TP8621B |  | H | TP8675
|  |  | redundant | TP8621Br |  | redundant | TP8675r

## Solenoid BOM
No. | Item | Mfg | PN | Qty | Vendor | Quote Unit Price | Total Est. Price | Date Ordered | Date Expected | PR# | Total Acutal Price | Location | NOTES:
1 | Rack | - | - | 1 | ? | 0 | 0 | N/A |  | N/A |  | Hall B | Already on hand
2 | Back Panel |  |  | 3 |  | 300 | 900 | [5 empty] | Guess
3 | 10-Slot Chassis | Allen Bradley | 1756-A10 | 2 | EECO | 478.04 | 956.08
4 | Power Supply | Allen Bradley | 1756-PA72 | 2 | EECO | 708.18 | 1416.36
5 | PLC | Allen Bradley | 1756-L72 | 1 | EECO | 5964.4 | 5964.4
6 | Ethernet Module | Allen Bradley | 1756-EN2T | 2 | EECO | 2123.8 | 4247.6
7 | Ethernet Gateway | Allen Bradley | 1756-EWEB | 1 | EECO | 2331 | 2331 | [5 empty] | May not be necessary
8 | Digital Relay Output Module (16 ch) | Allen Bradley | 1756-OW16I | 3 | EECO | 485.44 | 1456.32
9 | RTB Jumper for OW16I | Allen Bradley | 1756-JMPR | 3 | EECO | 5 | 15 | [5 empty] | Estimated Price
10 | Analog Input Module (16 ch) | Allen Bradley | 1756-IF16 | 1 | EECO | 1206.2 | 1206.2
11 | Digital Input Module, 24 VDC Sink | Allen Bradley | 1756-IB32 | 1 | EECO | 396.26 | 396.26 | [5 empty] | Estimated Price
12 | Sequence of Events Module | Allen Bradley | 1756-IB16ISOE | 1 | EECO | 664.52 | 664.52
13 | Analog Output Module (8 ch) | Allen Bradley | 1756-OF8 | 3 | EECO | 1554 | 4662
14 | Module Terminal Block (16 ch) | Allen Bradley | 1756-TBCH | 9 | EECO | 65.12 | 586.08
15 | Module Terminal Block (8 ch) | Allen Bradley | 1756-TBNH | 3 | EECO | 52.54 | 157.62
16 | Slot Filler | Allen Bradley | 1756-N2 | 6 | EECO | 25 | 150 | [5 empty] | Estimated Price
17 | TCP to Ethernet/IP | Real Time Automation | 490-NBX | 1 | Real Time Automation | 715 | 715 | [5 empty] | Could also be 460ETCTCP (does parsing), same price
18 | RS232 to Ethernet/IP | Real Time Automation | 435-NBX | 1 | Real Time Automation | 715 | 715
19 | LVDT Excitation/Readback | Macro Sensors | LVC-2500 | 4 | Macro Sensors | 521 | 2084
20 | CryoCon Temperature Monitor (8 ch) | CryoCon | 18C | 3 | CryoCon | 1695 | 5085
21 | CryoCon Panel Mount Kit | CryoCon | 3014-020 | 3 | CryoCon | 30 | 90
22 | 24 VDC Power Supply | RHINO | PSM24-360S | 4 | Automation Direct | 229 | 916
23 | 24VDC Redundancy Module | RHINO | PSM24-REM360S | 2 | Automation Direct | 159 | 318
24 | 15 Amp Circuit Breaker | Allen Bradley | 1492-CB1G150 | 2 | EECO | 43.99 | 87.98
25 | 5 Amp Circuit Breaker | Allen Bradley | 1492-CB1G050 | 18 | EECO | 46.08 | 829.44
26 | 2 Amp Circuit Breaker | Allen Bradley | 1489-M1C020 | 4 | EECO | 46.08 | 184.32
27 | Terminal block single level | Allen Bradley | 1492-J3 | 20 | EECO | 0.75 | 15
28 | Grounding Block | Allen Bradley | 1492-JG3 | 50 | EECO | 5.51 | 275.5
29 | End Barrier for J3 | Allen Bradley | 1492-EBJ3-Y | 20 | EECO | 0.76 | 15.2
30 | End Anchor for J3 | Allen Bradley | 1492-EAHJ35 | 12 | EECO | 4.37 | 52.44
31 | Terminal group marker | Allen Bradley | 1492-GM35 | 10 | EECO | 3.99 | 39.9
32 | Terminal block 2 level | Allen Bradley | 1492-JDG3 | 50 | EECO | 5.82 | 291
33 | Terminal block 2 level | Allen Bradley | 1492-JD3-RE | 50 | EECO | 8.39 | 419.5
34 | Terminal block 2 level | Allen Bradley | 1492-JD3-BL | 50 | EECO | 8.39 | 419.5
35 | Terminal block 2 level | Allen Bradley | 1492-JD3-W | 50 | EECO | 8.39 | 419.5
36 | Terminal block 2 level | Allen Bradley | 1492-JD3-Y | 50 | ON-HAND | 3.62 | 181
37 | End Barrier for JD3 | Allen Bradley | 1492-EBJD3 | 20 | EECO | 0.83 | 16.6
38 | End Barrier for JD3 | Allen Bradley | 1492-EBJ3 | 2 | EECO | 0.83 | 1.66
39 | End anchor for JD3 | Allen Bradley | 1492-EAHJ35 | 29 | EECO | 4.37 | 126.73
40 | 10 Screw Center Jumper | Allen Bradley | 1492-CJJ5-10 | 10 | EECO | 5 | 50 | [5 empty] | price guess
41 | End Barrier for JG3 | Allen Bradley | 1492-EBJ3-Y | 50 | EECO | 2.3 | 115
42 | Terminal block 3 level | Allen Bradley | 1492-WTF3 | 168 | EECO | 8.39 | 1409.52
43 | End Barrier for WTF3 | Allen Bradley | 1492-EBTF3 | 12 | EECO | 1.74 | 20.88
44 | End Anchor for WTF3 | Allen Bradley | 1492-EAHJ35 | 23 | EECO | 4.37 | 100.51
45 | 3 level + ground | Allen Bradley | 1492-JT3M | 77 | EECO | 5.4 | 415.8
46 | End Barrier for JT3M | Allen Bradley | 1492-EBJ3TM | 5 | EECO | 1.42 | 7.1
47 | Jumpers, 20 pole Red | Allen Bradley | 1492-SJT5-20-R | 10 | EECO | 9.32 | 93.2
48 | Jumpers, 20 pole Blue | Allen Bradley | 1492-SJT5-20-B | 10 | EECO | 9.32 | 93.2
49 | DIN Rail | Allen Bradley | 199-DR1 | 9 | EECO | 10.83 | 97.47
50 | Wire Duct | Panduit | 2X4LG6 | 120 | BEST PRICE | 10 | 1200
51 | 10" Touch Panel (Local Control Panel for EVs) | Automation Direct | EA9-T10CL | 1 | Automation Direct | 1290 | 1290
52 | Touch Panel Software | Automation Direct | EA9-PGMSW | 0 | Automation Direct | 99 | 0
53 | Ethernet Switch | Cisco | ?? | 1 | ?? | 5000 | 5000 | [5 empty] | Guess, based on Hall D's switch purchase
54 | UPS | APC | SMX2000RMLV2U | 1 | Newegg | 1159.99 | 1159.99
55 | Relay Smartcard for UPS | APC | AP9613 | 1 | TigerDirect | 200 | 200
56 | Vertical Power Strip | Hammond | 1587T10A1 | 2 | Allied Electronics | 84.62 | 169.24
57 | AMI Liquid Level Monitor | AMI | 135 | 2 | AMI | 835 | 1670
58 | AMI Liquid Level Probe | AMI | 135 | 2 | AMI | 1500 | 3000
59 | Timer Relay (for watchdog) | Tyco | CNT-35-96 | 1 |  | 225 | 225
60 | Relay for SOE (relay + base) | Finder | 44.62.7.024.4000 | 26 |  | 30 | 780
61 | Relay for EV's (relay + base + diode module) | Finder | 95.75 SMA | 26 |  | 30 | 780
TOTALS | [6 empty] | 56284.62 | (rack hardware)
[7 empty] | 0 | (cables, $500/cable)
[6 empty] | Total | 56284.62
What's missing?
Spares
|  |  | Hookup wire….maybe $1000 |  |  | Panel wiring
[5 empty] | Includes guess on missing stuff |  | 58284.62
???Other Stuff???
Fast DAQ Prices
Signal Conditioning
Fast DAQ itself
software?
Wiring?
Voltage tap wires?
Temp/Strain Cables?
Current Limiting Resistor Box?
Voltage tap distribution box?

## Solenoid Magnet Wire Map
| Distribution Box Instruments - Sensor Connector Wire Map CM-8501A | [5 empty] | Silicone Diode | Temperatures
Distribution Box Instruments - Vacuum Port 8501A
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Silicone Diodes |  | SPLICE | Connector # 8501A5 | Connector # 8501A4 | Connector # 8501A3 |  | Connector # 8501A2 | Connector # 8501A1 | Cable
|  | TRANSITION | FTACIR32V | IFDRG327013 | FTACIR32AC |  | MS3476L20-41PY | MS3470L20-41SY | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
TR8674 | I + | CLR / YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK / BLK | B | B | B | 2 | B | B | BLU
| V- | GRN/ GRN | C | C | C | 3 | C | C | BLK
| I- | RED / RED | D | D | D | 4 | D | D | BLK
TD8512r | I + | CLR / YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK / BLK | F | F | F | 6 | F | F | BLK
| V- | GRN/ GRN | G | G | G | 7 | G | G | GRN
| I- | RED / RED | H | H | H | 8 | H | H | RED
TD8513S | I + | CLR / YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK / BLK | K | K | K | 10 | K | K | BLU
| V- | GRN/ GRN | L | L | L | 11 | L | L | BLK
| I- | RED / RED | M | M | M | 12 | M | M | BLK
TD8513Sr | I + | CLR / YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK / BLK | P | P | P | 14 | P | P | BLK
| V- | GRN/ GRN | R | R | R | 15 | R | R | GRN
| I- | RED / RED | S | S | S | 16 | S | S | RED
TD8513T | I + | CLR / YEL | T | T | T | 17 | T | T | WHT
| V+ | BLK / BLK | U | U | U | 18 | U | U | BLU
| V- | GRN/ GRN | V | V | V | 19 | V | V | BLK
| I- | RED / RED | W | W | W | 20 | W | W | BLK
TD8513r | I + | CLR / YEL | X | X | X | 21 | X | X | BLK
| V+ | BLK / BLK | Y | Y | Y | 22 | Y | Y | BLK
| V- | GRN/ GRN | Z | Z | Z | 23 | Z | Z | GRN
| I- | RED / RED | a | a | a | 24 | a | a | RED
|  |  | b | b | b | 25 | b | b
|  |  | c | c | c | 26 | c | c
|  |  | d | d | d | 27 | d | d
|  |  | e | e | e | 28 | e | e
|  |  | f | f | f | 29 | f | f
|  |  | g | g | g | 30 | g | g
Cable interlock | 24 VDC | ORG | <h> | <h> | <h> | 31 | <h> | <h> | RED
Cable interlock | 24 VDC | ORG | <j> | <j> | <j> | 32 | <j> | <j> | BLK
| Distribution Box - Sensor Connector Wire Map CM-8501B | [5 empty] | Silicon Diode | Temperatures
Distribution Box Instruments - Vacuum Port 8501B
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Silicon Diodes |  | SPLICE | Connector # 8501B5 | Connector # 8501B4 | Connector # 8501B3 |  | Connector # 8501B2 | Connector # 8501B1 | Cable
|  | TRANSITION | FTACIR32V | IFDRG327013 | FTACIR32AC | > | MS3476L18-32PX | MS3470L18-32SX | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
#REF! | I + | CLR / YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK / BLK | B | B | B | 2 | B | B | BLU
| V- | GRN/ GRN | C | C | C | 3 | C | C | BLK
| I- | RED / RED | D | D | D | 4 | D | D | BLK
#REF! | I + | CLR / YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK / BLK | F | F | F | 6 | F | F | BLK
| V- | GRN/ GRN | G | G | G | 7 | G | G | GRN
| I- | RED / RED | H | H | H | 8 | H | H | RED
#REF! | I + | CLR / YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK / BLK | K | K | K | 10 | K | K | BLU
| V- | GRN/ GRN | L | L | L | 11 | L | L | BLK
| I- | RED / RED | M | M | M | 12 | M | M | BLK
#REF! | I + | CLR / YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK / BLK | P | P | P | 14 | P | P | BLK
| V- | GRN/ GRN | R | R | R | 15 | R | R | GRN
| I- | RED / RED | S | S | S | 16 | S | S | RED
#REF! | I + | CLR / YEL | T | T | T | 17 | T | T | WHT
| V+ | BLK / BLK | U | U | U | 18 | U | U | BLU
| V- | GRN/ GRN | V | V | V | 19 | V | V | BLK
| I- | RED / RED | W | W | W | 20 | W | W | BLK
#REF! | I + | CLR / YEL | X | X | X | 21 | X | X | BLK
| V+ | BLK / BLK | Y | Y | Y | 22 | Y | Y | BLK
| V- | GRN/ GRN | Z | Z | Z | 23 | Z | Z | GRN
| I- | RED / RED | a | a | a | 24 | a | a | RED
|  |  | b | b | b | 25 | b | b
|  |  | c | c | c | 26 | c | c
|  |  | d | d | d | 27 | d | d
|  |  | e | e | e | 28 | e | e
|  |  | f | f | f | 29 | f | f
|  |  | g | g | g | 30 | g | g
Cable interlock | 24 VDC | ORG | <h> | <h> | <h> | 31 | <h> | <h> | RED
Cable interlock | 24 VDC | ORG | <j> | <j> | <j> | 32 | <j> | <j> | BLK
| Distribution Box - Sensor Connector Wire Map CM-8502A | [5 empty] | Platinum Resistors | Temperatures
Distribution Box Instruments - Vacuum Port 8502A
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Platinum Resistors |  | SPLICE | Connector # 8502A5 | Connector # 8502A4 | Connector # 8502A3 |  | Connector # 8502A2 | Connector # 8502A1 | Cable
|  | TRANSITION | FTACIR32V | IFDRG327013 | FTACIR32AC | > | MS3476L18-32PX | MS3470L18-32SX | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
TP8621B | I + | YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK | B | B | B | 2 | B | B | BLU
| V- | GRN | C | C | C | 3 | C | C | BLK
| I- | RED | D | D | D | 4 | D | D | BLK
TP8621Br | I + | YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK | F | F | F | 6 | F | F | BLK
| V- | GRN | G | G | G | 7 | G | G | GRN
| I- | RED | H | H | H | 8 | H | H | RED
#REF! | I + | YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK | K | K | K | 10 | K | K | BLU
| V- | GRN | L | L | L | 11 | L | L | BLK
| I- | RED | M | M | M | 12 | M | M | BLK
#REF! | I + | YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK | P | P | P | 14 | P | P | BLK
| V- | GRN | R | R | R | 15 | R | R | GRN
| I- | RED | S | S | S | 16 | S | S | RED
TP8676A | I + | YEL | T | T | T | 17 | T | T | WHT
| V+ | BLK | U | U | U | 18 | U | U | BLU
| V- | GRN | V | V | V | 19 | V | V | BLK
| I- | RED | W | W | W | 20 | W | W | BLK
TP8676Ar | I + | YEL | X | X | X | 21 | X | X | BLK
| V+ | BLK | Y | Y | Y | 22 | Y | Y | BLK
| V- | GRN | Z | Z | Z | 23 | Z | Z | GRN
| I- | RED | a | a | a | 24 | a | a | RED
|  |  | b | b | b | 25 | b | b
|  |  | c | c | c | 26 | c | c
|  |  | d | d | d | 27 | d | d
|  |  | e | e | e | 28 | e | e
|  |  | f | f | f | 29 | f | f
|  |  | g | g | g | 30 | g | g
Cable interlock | 24 VDC | ORG | <h> | <h> | <h> | 31 | <h> | <h> | RED
Cable interlock | 24 VDC | ORG | <j> | <j> | <j> | 32 | <j> | <j> | BLK
| Distribution Box - Sensor Connector Wire Map CM-8502B | [5 empty] | Platinum Resistors | Temperatures
Distribution Box Instruments - Vacuum Port 8502B
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Platinum Resistors |  | SPLICE | Connector # 8502B5 | Connector # 8502B4 | Connector # 8502B3 |  | Connector # 8502B2 | Connector # 8502B1 | Cable
|  | TRANSITION | FTACIR32V | IFDRG327013 | FTACIR32AC | > | MS3476L18-32PX | MS3470L18-32SX | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
0 | I + | YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK | B | B | B | 2 | B | B | BLU
| V- | GRN | C | C | C | 3 | C | C | BLK
| I- | RED | D | D | D | 4 | D | D | BLK
0r | I + | YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK | F | F | F | 6 | F | F | BLK
| V- | GRN | G | G | G | 7 | G | G | GRN
| I- | RED | H | H | H | 8 | H | H | RED
#REF! | I + | YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK | K | K | K | 10 | K | K | BLU
| V- | GRN | L | L | L | 11 | L | L | BLK
| I- | RED | M | M | M | 12 | M | M | BLK
#REF! | I + | YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK | P | P | P | 14 | P | P | BLK
| V- | GRN | R | R | R | 15 | R | R | GRN
| I- | RED | S | S | S | 16 | S | S | RED
#REF! | I + | YEL | T | T | T | 17 | T | T | WHT
| V+ | BLK | U | U | U | 18 | U | U | BLU
| V- | GRN | V | V | V | 19 | V | V | BLK
| I- | RED | W | W | W | 20 | W | W | BLK
#REF! | I + | YEL | X | X | X | 21 | X | X | BLK
| V+ | BLK | Y | Y | Y | 22 | Y | Y | BLK
| V- | GRN | Z | Z | Z | 23 | Z | Z | GRN
| I- | RED | a | a | a | 24 | a | a | RED
|  |  | b | b | b | 25 | b | b
|  |  | c | c | c | 26 | c | c
|  |  | d | d | d | 27 | d | d
|  |  | e | e | e | 28 | e | e
|  |  | f | f | f | 29 | f | f
|  |  | g | g | g | 30 | g | g
Cable interlock | 24 VDC | ORG | <h> | <h> | <h> | 31 | <h> | <h> | RED
Cable interlock | 24 VDC | ORG | <j> | <j> | <j> | 32 | <j> | <j> | BLK
| Distribution Box - Sensor Connector Wire Map CM-8503A | [5 empty] | Platinum Resistors | Temperatures
Distribution Box Instruments - Vacuum Port 8503A
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Platinum Resistors |  | SPLICE | Connector # 8503A5 | Connector # 8503A4 | Connector # 8503A3 |  | Connector # 8503A2 | Connector # 8503A1 | Cable
|  | TRANSITION | FTACIR19V | IFDRG197013 | FTACIR19AC | > | MS3476L18-32PX | MS3470L18-32SX | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
#REF! | I + | YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK | B | B | B | 2 | B | B | BLU
| V- | GRN | C | C | C | 3 | C | C | BLK
| I- | RED | D | D | D | 4 | D | D | BLK
#REF! | I + | YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK | F | F | F | 6 | F | F | BLK
| V- | GRN | G | G | G | 7 | G | G | GRN
| I- | RED | H | H | H | 8 | H | H | RED
#REF! | I + | YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK | K | K | K | 10 | K | K | BLU
| V- | GRN | L | L | L | 11 | L | L | BLK
| I- | RED | M | M | M | 12 | M | M | BLK
#REF! | I + | YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK | P | P | P | 14 | P | P | BLK
| V- | GRN | R | R | R | 15 | R | R | GRN
| I- | RED | S | S | S | 16 | S | S | RED
|  |  | T | T | T | 17 | T | T
Cable interlock | 24 VDC | ORG | <U> | <U> | <U> | 18 | <U> | <U> | RED
Cable interlock | 24 VDC | ORG | <V> | <V> | <V> | 19 | <V> | <V> | BLK
OBSOLETE!

## LabView Chassis1Config File
Chassis | Tye (TR, SG,…) | Read Register Address | Write Register Address | LC Tag (DINT) | Ecitation (uA or V) | Serial #
1 | LC | 68 | 30 | LC_From_cRIO[1] | 2.5 | 200610240
1 | LC | 69 | 31 | LC_From_cRIO[2] | 2.5 | 310292
1 | LC | 6a | 32 | LC_From_cRIO[3] | 2.5 | 200610239
1 | LC | 6b | 33 | LC_From_cRIO[4] | 2.5 | 310291
1 | LC | 6c | 34 | LC_From_cRIO[5] | 2.5 | 200610235
1 | LC | 6d | 35 | LC_From_cRIO[6] | 2.5 | 310288
1 | LC | 6e | 36 | LC_From_cRIO[7] | 2.5 | 200610233
1 | LC | 6f | 37 | LC_From_cRIO[8] | 2.5 | 310287
1 | PT | 48 | 10 | T_From_CRIO[1] | 2.5 | 31432
1 | PT | 49 | 11 | T_From_CRIO[2] | 2.5 | 31433
1 | PT | 4a | 12 | T_From_CRIO[3] | 2.5 | 31444
1 | PT | 4b | 13 | T_From_CRIO[4] | 2.5 | 31491
1 | PT | 4c | 14 | T_From_CRIO[5] | 2.5 | 32302
1 | PT | 4d | 15 | T_From_CRIO[6] | 2.5 | 32304
1 | PT | 4e | 16 | T_From_CRIO[7] | 2.5 | 32305
1 | PT | 4f | 17 | T_From_CRIO[8] | 2.5 | 32306
1 | PT | 50 | 18 | T_From_CRIO[9] | 2.5 | 32307
1 | PT | 51 | 19 | T_From_CRIO[10] | 2.5 | 32308
1 | PT | 52 | 1a | T_From_CRIO[11] | 2.5 | 32310
1 | PT | 53 | 1b | T_From_CRIO[12] | 2.5 | 32311
1 | PT | 54 | 1c | T_From_CRIO[13] | 2.5 | 32315
1 | PT | 55 | 1d | T_From_CRIO[14] | 2.5 | 32314
1 | TR | 38 | 0 | TR_From_cRIO[1] | 2.5 | 100007
1 | TR | 39 | 1 | TR_From_cRIO[2] | 2.5 | 99799
1 | TR | 3a | 2 | TR_From_cRIO[3] | 2.5 | 99776
1 | TR | 3b | 3 | TR_From_cRIO[4] | 2.5 | 99801
1 | TR | 3c | 4 | TR_From_cRIO[5] | 2.5 | 99453
1 | TR | 3d | 5 | TR_From_cRIO[6] | 2.5 | 101015
1 | TR | 3e | 6 | TR_From_cRIO[7] | 2.5 | 100862
1 | TR | 3f | 7 | TR_From_cRIO[8] | 2.5 | 99452
1 | TR | 40 | 8 | TR_From_cRIO[9] | 2.5 | 101013
1 | TR | 42 | a | TR_From_cRIO[10] | 2.5 | 101016
1 | TR | 43 | b | TR_From_cRIO[11] | 2.5 | 99428
1 | TR | 44 | c | TR_From_cRIO[12] | 2.5 | 101014
1 | TR | 45 | d | TR_From_cRIO[13] | 2.5 | 110276
1 | TR | 46 | e | TR_From_cRIO[14] | 2.5 | 110277
1 | TR | 47 | f | TR_From_cRIO[15] | 2.5 | 109521

## LabView Chasis2 Config File
Chassis | Tye (TR, SG,…) | Read Register Address | Write Register Address | LC Tag (DINT) | Ecitation (uA or V) | Serial #
2 | LC | 68 | 30 | LC_From_cRIO[9] | 2.5 | 200610237
2 | LC | 69 | 31 | LC_From_cRIO[10] | 2.5 | 310290
2 | LC | 6a | 32 | LC_From_cRIO[11] | 2.5 | 201610067
2 | LC | 6b | 33 | LC_From_cRIO[12] | 2.5 | 310293
2 | LC | 6c | 34 | LC_From_cRIO[13] | 2.5 | 200610236
2 | LC | 6d | 35 | LC_From_cRIO[14] | 2.5 | 310289
2 | LC | 6e | 36 | LC_From_cRIO[15] | 2.5 | 200610232
2 | LC | 6f | 37 | LC_From_cRIO[16] | 2.5 | 310277
2 | PT | 48 | 10 | T_From_CRIO[15] | 2.5 | 32316
2 | TR | 38 | 0 | TR_From_cRIO[16] | 2.5 | 109519
2 | TR | 39 | 1 | TR_From_cRIO[17] | 2.5 | 109522
2 | TR | 3a | 2 | TR_From_cRIO[18] | 2.5 | 109494
2 | TR | 3c | 4 | TR_From_cRIO[19] | 2.5 | 110279
2 | TR | 3d | 5 | TR_From_cRIO[20] | 2.5 | 109520
2 | TR | 3e | 6 | TR_From_cRIO[21] | 2.5 | 109493
2 | TR | 3f | 7 | TR_From_cRIO[22] | 2.5 | 110278
2 | TR | 40 | 8 | TR_From_cRIO[23] | 2.5 | 110290
2 | TR | 41 | 9 | TR_From_cRIO[24] | 2.5 | 110287
2 | TR | 42 | a | TR_From_cRIO[25] | 2.5 | 110289
2 | TR | 43 | b | TR_From_cRIO[26] | 2.5 | 110288
2 | HS |  |  | HS-From_CRIO[17] | 2.5