## Sheet1
Date: | 2017-02-27
By : | Pablo Campero and Renuka Rajput-Ghoshal
INSTRUMENTATION TEST PLC- EPICS PLAN
SOLENOID SERVICE TOWER - SST
Signal ID | Sensor Type | Calibrated - Tested | Installed | To be tested Now | To be Tested after | Action | Check | Set Point | ReadBack Controller | ReadBack PLC | ReadBack EPICS | Comments
TR8622A | Cernox | Yes | Yes | Yes |  | 1. Verify hardwiring - Use reference DWG 0649 & 0678 | √ | Temp Room ~ 300 [K] | 293.982 | 293.551 | 293.55
TR8622Ar |  | Yes | Yes |  |  | 2. Check sensor connection in the Cryocon unit - Use Cryocon maps | √ |  | 293.982 | 293.551 | 293.55
TR8622B |  | Yes | Yes |  |  | 3. Unplug DB9 connectors except sensor that is being checked in rear panel of Cryocon 1 | √ |  | 294.418 | 293.987 | 239.99
TR8622Br |  | Yes | Yes |  |  | 4. Verify if sensor position correspond to the channel assigned | √ |  | 294.418 | 293.987 | 239.99
TR8611 |  | Yes |  |  |  | 5. Check communication between 490-NBX module and PLC | √ |  | clip | 0 | 0
TR8611r |  | Yes |  |  |  | 6. Verify correct read-back values for the sensor in the PLC controller | √ |  | clip | 0 | 0
TR8672 |  | Yes |  |  |  | 7. Check communication between PLC and EPICS | √ |  | clip | 0 | 0 | Cryocon unit at Channel F has set an "Internal_Temp" sensor connected - this sensor does not appears on the documentation and 0678 dwg
TR8672r |  | Yes |  |  |  | 8. Use the Helium SST EPICS screen to verify and monitor the temperature sensor readings in [K] units | √ |  | clip | 0 | 0
TR8671 |  | Yes |  |  |  | 9. Record Read-back values - compare PLC and Cryocon Readings | √ |  | clip | 0 | 0
TR8671r |  | Yes |  |  |  | 10. Repeat the steps above with each temperature sensor | √ |  | clip | 0 | 0
TR8610 |  | No | [6 empty] | clip | 0 | 0
TR8610r |  | No | [6 empty] | clip | 0 | 0
TR8670 | Cernox | Yes |  | Yes |  | 1. Verify hardwiring - Use reference DWG 0649 & 0678 | √ | Temp Room ~ 300 [K] | clip | 0 | 0
TR8670r |  | Yes |  |  |  | 2. Check sensor connection in the Cryocon unit - Use Cryocon maps | √ |  | clip | 0 | 0
TR8673 |  | Yes |  |  |  | 3. Unplug DB9 connectors except sensor that is being checked in rear panel of Cryocon2 | √ |  | clip | 0 | 0
TR8673r |  | Yes |  |  |  | 4. Verify if sensor position correspond to the channel assigned | √ |  | clip | 0 | 0
TR8674 |  | Yes |  |  |  | 5. Check communication between 490-NBX module and PLC | √ |  | clip | 0 | 0
TR8674r |  | Yes |  |  |  | 6. Verify correct read-back values for the sensor in the PLC controller | √ |  | clip | 0 | 0
TR8624A |  | Yes |  |  |  | 7. Check communication between PLC and EPICS | √ |  | clip(blinking) | 0 | 0 | Cryocon unit at Channel D has set an "Not assigned" sensor connected - this sensor does not appears on the documentation and 0678 dwg
TR8624B |  | Yes |  |  |  | 8. Use the Helium SST EPICS screen to verify and monitor the temperature sensor readings in [K] units | √ |  | clip(blinking) | 0 | 0
TP8621A | PT- 100 | Yes |  |  |  | 9. Record Read-back values - compare PLC and Cryocon Readings | √ |  | clip | 0 | 0
TP8621Ar |  | Yes |  |  |  | 10. Repeat the steps above with each temperature sensor | √ |  | clip | 0 | 0
TP8621B |  | Yes | [6 empty] | clip | 0 | 0
TP8621Br |  | Yes | [6 empty] | clip | 0 | 0
TP8611 | PT- 100 | Yes | Yes | Yes |  | 1. Verify hardwiring - Use reference DWG 0649 & 0678 | √ | Temp Room ~ 300 [K] | 293.909 | 293.925 | 293.92
TP8611r |  | Yes | Yes |  |  | 2. Check sensor connection in the Cryocon unit - Use Cryocon maps | √ |  | 293.909 | 293.925 | 293.92
TP8620A |  | Yes | Yes |  |  | 3. Unplug DB9 connectors except sensor that is being checked in rear panel of Cryocon3 | √ |  | 294.201 | 294.229 | 294.23
TP8620Ar |  | Yes | Yes |  |  | 4. Verify if sensor position correspond to the channel assigned | √ |  | 294.201 | 294.229 | 294.23
TP8620B |  | Yes | Yes |  |  | 5. Check communication between 490-NBX module and PLC | √ |  | 293.984 | 294.018 | 294.02
TP8620Br |  | Yes | Yes |  |  | 6. Verify correct read-back values for the sensor in the PLC controller | √ |  | 293.984 | 294.018 | 294.02
TP8675 |  | Yes | Yes |  |  | 7. Check communication between PLC and EPICS | √ |  | 294.658 | 294.661 | 294.66
TP8675r |  | Yes | Yes |  |  | 8. Use the Helium SST EPICS screen to verify and monitor the temperature sensor readings in [K] units. | √ |  | 294.658 | 294.661 | 294.66
TP8622A |  | Yes | Yes |  |  | 9. Record Read-back values - compare PLC and Cryocon Readings | √ |  | 296.098 | 296.112 | 296.11
TP8622Ar |  | Yes | Yes |  |  | 10. Repeat the steps above with each temperature sensor | √ |  | 296.222 | 296.234 | 296.23
TP8622B |  | Yes | Yes | [5 empty] | 296.283 | 296.294 | 296.3
TP8622Br |  | Yes | Yes | [5 empty] | 296.158 | 296.167 | 296.17
PT8620 | Pressure |  | Yes | Yes (Initial Test) |  | 1. Verify hardwiring - Use reference DWG 0626 | √ | Pressure in Tanks w/o LHe | N/A | 1.363 | 1.36 | DWG 0626 need to be corrected (change scale range)
PT8670 |  |  | Yes |  |  | 2. Ensure proper power source (24 VDC ) to the Pressure Transducers | √ |  | N/A | 2.074 | 2.07
PT8675A |  |  | No |  | Yes | 3.Verify coinfiguration/ scaling factors PLC Input module | √ |  |  |  |  | Change scale factor to PT8620 Range: 0-75 psi
PT8677 |  |  | No |  | Yes | 4. Verify correct read-back values for the sensor in the PLC controller | √ |  |  |  |  | Change scale factor to pt8670 Range: 0-50 psi
[6 empty] | 5. Check communication between PLC and EPICS | √
[6 empty] | 6. Use the Helium - SST EPICS screen to verify and monitor the pressure readings in Atma | √
[6 empty] | 7. Record Read-back values | √
[6 empty] | 8. Repeat the steps above with each Presure transducer | √
LL8620DP_raw | Differential Pressure |  | Yes | Yes |  | 1. Verify hardwiring - Use reference DWG 0626 | √ | 0 [In H2O] | N/A | 0.029 [In H2O] | N/A | DWG 0626 need to be corrected (change scale range)
LL8670DP_raw |  |  | Yes |  |  | 2. Ensure proper power source (24 VDC) to the DP | √ | 0 [In H2O] | N/A | - 0.152 [In H2O] | N/A
LL8620DP | Differential Pressure |  | Yes | Yes |  | 3.Verify coinfiguration/ scaling factors PLC module | √ | 0% | N/A | -23.86% | -23.86% | Input row to the DP8620 & DP8670 requires filters on PLC code
LL8670DP |  |  | Yes |  |  | 4. Differential pressure transducer are used to mesurre LHe level in reservoirs/ check formula used in PLC logic | √ | 0% | N/A | -76.6% | -76.6%
[6 empty] | 5. Verify correct read-back values for the sensor in the PLC controller | √
[6 empty] | 6. Check communication between PLC and EPICS | √
[6 empty] | 8. Use the Helium - SST EPICS screen to verify and monitor the LHE Liquid level SC in % units. | √
[6 empty] | 8. Record Read-back values | √
[6 empty] | 9. Repeat the steps above with the DP sensor | √
LL8629SC | Liquid Level |  | Yes | No |  | 1. Verify hardwiring - Use reference DWG 0659 & 0628 | [5 empty] | Check with Dave K.
LL8670SC |  |  | Yes |  |  | 2. Ensure proper 24 VDC COM for the LL-SC sensors
3. Check configuration(Output signals, Set points, limit levels) in the AMI 135 controller - Use Level measurments on [%].
4.Verify coinfiguration/ scaling factors (0-10V) Analog Input PLC module
5. Differential pressure transducer are used to mesurre LHe level in reservoirs/ check cryo-formula used in PLC logic
6. Verify correct read-back values for the sensor in the PLC controller
7. Check communication between PLC and EPICS
8. Use the Helium - SST EPICS screen to verify and monitor the LHE Liquid level SC in % units.
8. Record Read-back values
9. Repeat the steps above with each LL-SC sensor
FI8621A | Flow Meters |  | No | No |  | 1. Verify hardwiring - Use reference DWG 0660, 0627 & 0624 | √ |  |  |  |  | No flow at the moment
FI8621B |  |  | No |  |  | 2. Ensure proper 24 VDC voltage source for the Mass Flow controller | √
3. Check configuration(Output/Input signals, Set points, limit levels) in the TELEDYNE Mass Flow controller
4. Verify coinfiguration/ scaling factors (4-20mA) Analog Output PLC module
5.Verify coinfiguration/ scaling factors (4-20mA) Analog Input PLC module
6. Verify correct read-back values for the sensor in the PLC controller
7. Check communication between PLC and EPICS
8. Use the Helium - SST EPICS screen to verify and monitor the Lead Flow in [SLPM] units.
8. Record Read-back values
9. Repeat the steps above with each flow meter
EV8611CD | EV- Valves |  | Yes | Yes |  | 1. Verify hardwiring - Use reference DWG 0638 & 0650 | √ | 50% | N/A | 51.02% | 51.02%
EV8670BY |  |  | Yes |  |  | 2. Ensure proper power source 24 V DC - Use Reference DWG 0637 | √ |  | N/A | 50.8% | 50.81%
EV8611JT |  |  | Yes |  |  | 3.Verify PLC Relay Outputs - configuration 0-24 VDC | √ |  | N/A | 51.05% | 51.05%
EV8612 |  |  | Yes |  |  | 4.Verify configuration switch on the LVDT's and check that belongs to the valve respectevely - Use DWG 0651 and 0627 | √ |  | N/A | 50.97% | 50.97%
EV8611CD_LVDT |  |  | Yes |  |  | 5. Verify analog Input PLC module configuration- scale factor (4-20mA) | √
EV8670BY_LVDT | LVDT's |  | Yes | Yes |  | 6. Check communication between PLC and EPICS | √
EV8611JT_LVDT |  |  | Yes |  |  | 7. Valves have a PID control/ Check Mode (Manual) to control OPEN/CLOSE | √
EV8612_LVDT |  |  | Yes |  |  | 8. Use PID Set parameters EPICS screen to set Normal mode and set point valve | √
` | [5 empty] | 10. Verify correct read-back values for LVDT'S the PLC controller | √
[6 empty] | 11. Ensure the correct PID response in the PLC logic. | √
[6 empty] | 12. Verify Relay output indicators to OPEN an CLOSE the valve | √
[6 empty] | 13. Use the Helium - SST EPICS screen to verify the % of open and close indicators in the valve | √
[6 empty] | 14. Record Read-back values | √
[6 empty] | 15. Repeat the steps above with each EV and LVDT | √
SV8622 | SV - Valves |  | No | Yes |  | 1. Verify hardwiring - Use reference DWG 0640
SV8678CR |  |  | No |  |  | 2. Ensure proper power source 24 V DC
SV8678DV |  |  | No |  |  | 3.Verify PLC Relay Outputs - configuration 0-24 VDC
SV8675BY |  |  | No |  |  | 4. Force bit in the PLC expert screen to OPEN and CLOSE the Valve
5. Check communication between PLC and EPICS
6. Use the Helium - SST EPICS screen to verify the open/close valve indicators (Green - open)
7. Record Read-back values (OPEN/CLOSE)
8. Repeat the steps above with each SV
PV8674 | PV- Valve |  | Yes | Yes |  | 1. Verify hardwiring - Use reference DWG 0623 | √ | 1 = Open 0 = Close | N/A | 1 = Open 0 = Close | Needs to be updated to on/off valve | Wiring corrected output signal for the PV, was change from Analog output PLC module to a Relay output module channel 15 - DWG 0640 and 0623 have to be updated
[6 empty] | 2. Ensure proper power source 24 V DC | √
[6 empty] | 3. Check pressure stable for the air supply in the valve | √
[6 empty] | 4.Verify Analog Outputs - configuration (0-10 v/4-20 mA) | √
[6 empty] | 5. Force bit in the PLC expert screen to OPEN and CLOSE the Valve | √
[6 empty] | 6. Check communication between PLC and EPICS | X
[6 empty] | 7. Use the Helium - SST EPICS screen to verify the open/close valve indicators (Green - open) | √ |  |  |  |  | Valve need to be changed to OPEN/CLOSE indicator on EPICS
[6 empty] | 8. Record Read-back values (OPEN/CLOSE) | √ |  |  |  |  | Air supply to the PV was fixed by swaping air connector in the valve
HT8621A | Heater | Yes | Yes | No |  | 1. Verify hardwiring - Use reference DWG 0638 | √ |  |  |  |  | Check power levels with Dave K.
HT8621B |  | Yes | Yes |  |  | 2. Ensure proper power source 24 V DC | √
3.Verify Relay Outputs - configuration module
4.Check thresholds on the lead temperatures A and B.
5. Force bit in the PLC expert screen to turn ON/OFF the Heaters
6. Check communication between PLC and EPICS
7. Use the Helium - SST EPICS screen to verify ON/OFF heater indicators (Green light On)
8. Record Read-back values
9.. Repeat the steps above with each heater
HTR8620 | Heater | Yes | Yes | Yes (Initial test) |  | 1. Verify hardwiring - Use reference DWG 0638, 0661, 0624 & 0627 | √ |  |  |  |  | Need to be Cold before checking. - Talk to Dave K. to confirm
HTR8672 |  | Yes | YES |  |  | 2. Ensure proper power source 120 VAC to the power supply Sorensen | √
[6 empty] | 3. Check configuration(Output signals, Set points, limit levels) in the SORENSEN DLM 600W power supply - Use 4-20 mA switch configuration | √
4. Verify coinfiguration/ Relay Output & analog output PLC module
[6 empty] | 5.Verify coinfiguration/ scaling factors (4-20mA) Analog Input PLC module | √
[6 empty] | 6. Check communication between PLC and EPICS | x |  |  |  |  | Heaters on SST-Helium have to be update and replaced in the PID control EPICS screns, they display Torus heaters at the moment
7. Heater has a PID control/ Check Mode (Manual) to control the heater
8. Use PID Set parameters EPICS screen to set Normal mode and set a test value for the Heater
9. Force bit in the PLC expert screen to turn ON/OFF the heater
[6 empty] | 10. Verify correct read-back values for volatge and current for the heaters in the PLC controller | [5 empty] | Configured and tested Heater power supplies
11. Ensure the correct PID response in the PLC logic.
12. Verify Relay output indicators to ON/OFF
13. Use the Helium - SST EPICS screen to verify the Heater is ON OR OFF, check % read back values and compare with the set point
14. Record Read-back values
15. Repeat the steps above with each Heater
VACUUM SIGNALS
CG8606 | gauge |  |  | No |  | 1. Verify hardwiring - Use reference DWG 0628 & 0656 | [5 empty] | Controller and Vacuum pump need to be operational first to test this signals
CG8600TB | [5 empty] | 2. Ensure proper 120 ADC voltage source for the Vacuum controller and Instrumentation
TB8600 (TURBO) | pump speed |  |  |  |  | 3. Check configuration(Analog output/Input signals, Set points, limit levels) in the PFIFER TPG 362 controller
4. Verify coinfiguration/ scaling factors (0-10 V) Analog Input PLC module
5. Verify correct read-back values for thegauges in the PLC controller
6. Check communication between PLC and EPICS
7. Use the Vaccum Sytem EPICS screen to verify and monitor vacum signals [Torr] units.
8. test Alarm handler for the vaccum threshold established - Use EPICS Handler
9. Record Read-back values
10. Repeat the steps above with each vacuum signal
PV8600 | PV- Valve |  |  | No |  | 1. Verify hardwiring - Use reference DWG 0641 & 0656 | [5 empty] | Controller and Vacuum pump need to be operational first to test this signals
2. Ensure proper power source 24 V DC
3. Check pressure stable for the air supply in the valve
4.Verify Discrete Input PLC Module - configuration (0-30V)
5. In the PLC expert screen verify the readback switch position OPEN and CLOSE for the Valve
6. Check communication between PLC and EPICS
7. Use the Vaccum Sytem EPICS screen to verify and monitor the main vacum gate valve (OPEN/CLOSE)