## Sheet1
Solenoid SOE - Test Checkout
Relay Number | Event Checked | Hardware Relay | PLC SOE Module |  | MPS Dump Switch Open | EPICS - Interlock Status Screen | Coments
|  |  | Hardware- SOE Module Indicator Display | Software-PLC readout Indicator status
0 | Lead Temperature | ü | û | ü | ü | û | Assigned indicator do not change status on EPICS screen
1 | Liquid Helium Level 8620SC | ü | û | ü | ü | û | Assigned indicator do not change status on EPICS screen
2 | Liquid Helium Level 8670SC | ü | û | ü | ü | û | Assigned indicator do not change status on EPICS screen
3 | Crycon 1 | ü | û | ü | ü
4 | Crycon 2 | ü | û | ü | ü
5 | Spare | ü | Not tested | Not tested | Not tested | Not tested
6 | PLC Fast Dump | ü | û | ü | ü | ü
7 | Vacuum SUM Interlock | ü | û | ü | ü
8 | Watchdog | ü | ü | ü | ü | ü
9 | Current Lead Water Flow | Not tested | Not tested | Not tested | Not tested | Not tested | No circuit water flow at the moment
10 | VT Cable Intrerlock | Not tested | Not tested | Not tested | Not tested | Not tested
11 | System Cable Interlock | Not tested | Not tested | Not tested | Not tested | Not tested
12 | Quench Detector 1 | Not tested | Not tested | Not tested | Not tested | Not tested | Volatge has to be injected to test
13 | Quench Detector 2 | Not tested | Not tested | Not tested | Not tested | Not tested | Volatge has to be injected to test
14 | Spare | ü | Not tested | Not tested | Not tested | Not tested
15 | Spare | ü | Not tested | Not tested | Not tested | Not tested