## PID setup and check off
PID Group: | Phase of Operation:
S1 | 300K-100K cooldown of Solenoid 4K Cold Mass
Using 4 atm helium from ESR and the Liquid N2 in the DBX warm (300K) and cold (~80K) helium are mixed to a variable temperature to cool the Solenoid. Nitrogen system in the DBX must be fairly steady and liquid in the reservoir should be at 55% or greater. The level in the nitrogen reservoir in the DBX must not overflow into the other HX's or the temperatures will not be stable
Device to be controlled | Description | Mode | Manual Position | Input | Set val | Reverse or Direct or interlock | Max Pos | Min Pos | Max Chg | Min Chg | Sample Time (sec) | Kp | Ki | Kd | Gain Ratio Kp/(Ki*ST) (typ~3) | Date PID Verified to work | Verifying Persons Initials | Comments
PV8522SCD | Solenoid Warm Return Valve | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | -
PV8522SR | Solenoid Cold Return Valve | Manual | 0 | - | - | - | - | - | - | - | - | - | - | - | -
PV8563W | 300K Helium Supply Helium for Magnet Cooldown (or Warmup) | Normal | - | PT8565 | 2 to 2.8 | Direct (neg gains) | From PID | 0 | 10 | 0.1 | 3 | -30 | -1 | 0 | 10 |  |  | Simple
PV8563W.MAX | Max Postion of PV8563W | Normal | - | PV8563C.OVAL | 95 | Reverse (pos gains) | 100 | 0 | 0.3 | 0 | 600 | 2 | 0.001 | 0 | 3.3333 |  |  | Simple
PV8563W | 300K Helium Supply Helium for Magnet Cooldown (or Warmup) | Normal | - | P_CDHE_8563W_S | 0..3 | Direct (neg gains) | From PID | 0 | 10 | 0.1 | 3 | -30 | -1 | 0 | 10 |  |  | complex
PV8563W.MAX | Max Postion of PV8563W | Normal | - | PV8563C.OVAL | 95 | Reverse (pos gains) | 100 | 0 | 0.3 | 0 | 600 | 2 | 0.001 | 0 | 3.3333 |  |  | complex
PV8563C | 80K Helium Supply Helium for Magnet Cooldown (or Warmup) | Normal | - | HE_SMETAL_DT2 | 20 | Reverse | From PID | 0 | 5 | 0 | 300 | 0.3 | 0.0003 | 0 | 3.3333
PV8653C.MAX | 80K Helium Supply Helium for Magnet Cooldown Max position | Normal | - | S_DT_MAX_Percent | 75 to 90 | Reverse | 100 | 0 | 5 | 1 | 30 | 10 | 0.1 | 0 | 3.3333 |  |  | maximum highest percentage of allowable DT's
PV8563C | 80K Helium Supply Helium for Magnet Cooldown (or Warmup) | Normal | - | TD8513S | 220 | Direct | From PID | 0 | 5 | 0 | 300 | -0.3 | -0.0003 | 0 | 3.3333 |  |  | fixed temperature or manually steped temp
PV8653C.MAX | 80K Helium Supply Helium for Magnet Cooldown Max position | Normal | - | METAL4K_DT_MAX | 30 | Reverse | 100 | 0 | 5 | 1 | 30 | 10 | 0.1 | 0 | 3.3333 |  |  | fixed temperature or manually steped temp
PV86566S | Variable temperature supply to solenoid | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | -
PV8512S | 4K supply to Solenoid | Manual | 0 | - | - | - | - | - | - | - | - | - | - | - | -
PV8674 | Magnet Reservoir Return Isolation Valve | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | -
EV8670BY | Shield Bypass Valve | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | -
EV8670BY | Shield Bypass Valve | Normal | - | SSHLD_DP | 0.1 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
EV8553 | DBX Nitrogen Reservoir Fill Valve | Normal | - | LL8554CP | 55 | Reverse | From PID | From PID | 8 | 0.2 | 30 | 2 | 0.02 | 0 | 3.3333
EV8553.MIN | DBX Nitrogen Reservoir Fill Valve | Manual | 4.5 | HTR8554.OVAL | 3 |  | 5 | 3 | 15 | 0.05 | 100 | 0.1 | 0.0003 | 0 | 3.3333
EV8553.MAX | DBX Nitrogen Reservoir Fill Valve | Manual | 60 | LL8554CP | 60 |  | 60 | 6 | 5 | 0.2 | 15 | 10 | 0.2 | 0 | 3.3333
HTR8554 | Heater in DBX LN2 vessel | Normal | - | LL8554CP | 65 | Direct | 100 | 0 | 15 | 0 | 15 | -6 | -0.03 | 0 | 13.3333
HTR8554_Min1 | Heater in DBX LN2 vessel | Manual | 0 | - | - | - | - | - | - | - | - | - | - | - | -
PV8558 | DBX LN2 reservoir back pressure regulator | Normal | - | PT8554 | 1.2 | Direct (neg gains) | 100 | 0 | 5 | 0.3 | 10 | -300 | -10 | 0 | 3
EV8611JT | Lead Reservoir JT valve | Manual | 20 | - | - | - | - | - | - | - | - | - | - | - |  |  |  | To put a small trickle flow into the lead reservoir
EV8611JT | Lead Reservoir JT valve | Normal | - | FI8621A | 10 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | To put a small trickle flow into the lead reservoir
EV8612 | Magnet Reservoir Supply vlave | Manual | 10 | - | - | - | - | - | - | - | - | - | - | -
EV8611CD | Cooldown Valve (Magnet Annulus bottom fill) | Normal | - | FI8561 | 3 | Reverse (positive gains) | from PID | 0 | 3 | 0.2 | 10 | 3 | 0.1 | 0 | 3
EV8611CD.MAX | Cooldown Valve (Magnet Annulus bottom fill max position) | Normal | - | PT8670 | 1.3-2.0 | Direct (neg gains) | 100 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | Cascading PID to keep from overpowering CHL purifiers, could just choose a manual positoin or could use vaporizer HX8675 outlet temperature TP8675
EV8611CD | Cooldown Valve (Recooler bottom fill) OPTIONAL | Normal | - | CFI60DLP | 3 | Reverse | From PID | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | Optional way to limit the cooling flow rate
EV8611CD | Cooldown Valve (Recooler bottom fill) MAX OPTIONAL | Normal | - | CFI082 | 8-15 | Reverse | From PID | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | Cascading PID to keep from overpowering CHL purifiers, Could change to FI8561
EV8611CD.MAX | Cooldown Valve (Magnet Annulus bottom fill max position) | Normal | - | TP8675 | 285 |  | 100 | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | Cascading PID to keep from icing up the line out of the vaporizer (Option if needed)
PID Group: | Phase of Operation:
S2 | 100K-4K cooldown of Solenoid 4K Cold Mass
4K supercritical gas is used to cool and fill the Lead Reservoir and then liquid is withdrawn from the reservoir to cool the magnet
Device to be controlled | Description | Mode | Manual Position | Input | Set val | Reverse or Direct or interlock | Max Pos | Min Pos | Max Chg | Min Chg | Sample Time (sec) | Kp | Ki | Kd | Gain Ratio Kp/(Ki*ST) (typ~3) | Date PID Verified to work | Verifying Persons Initials | Comments
PV8522SCD | Solenoid Warm Return Valve | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | - |  |  | open until liquid collectsin the lead reservoir
PV8522SR | Solenoid Cold Return Valve | Manual | 0 | - | - | - | - | - | - | - | - | - | - | - | - |  |  | closed until liquid collectsin the lead reservoir
PV8522SCD | Solenoid Warm Return Valve | Manual | 0 | - | - | - | - | - | - | - | - | - | - | - | - |  |  | closed once the magnet has level in the lead reservoir
PV8522SR | Solenoid Cold Return Valve | Normal | - | PT8620 | 1.5 to 1.8 | Direct (Negative gains) | 100 | 0 | 3 | 0.2 | 10 | -30 | -1 | 0 | 3 |  |  | Use once the magnet has level in the lead reservoir
PV86566S | Variable temperature supply to solenoid | Manual | 0 | - | - | - | - | - | - | - | - | - | - | - | -
PV8512S | 4K supply to Solenoid | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | - |  |  | Open slowly to get the 4K SC gas to the supply valves in the SST
PV8674 | Magnet Reservoir Return Isolation Valve | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | -
EV8670BY | Shield Bypass Valve | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | -
EV8670BY | Shield Bypass Valve | Normal | - | SSHLD_DP | 0.1 | Direct (Negative gains) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
EV8611JT | Lead Reservoir JT valve | Normal | - | LL8620SC | 60 | Reverse (pos gains) | 60 | from PID | 5 | 0.2 | 200 | 1.7 | 0.002 | 0 | 4.25 |  |  | Primary Liquid fill Valve for leads
EV8611JT_MIN | Lead Reservoir JT valve | Normal | - | TR8610 | 5.5 | Reverse (pos gains) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | Min to keep U-tube from getting warm
EV8612 | Magnet Reservoir Supply vlave | Normal | - | TP8675A | 275 | Direct (Negative gains) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | Vaporizer overpowered temperature sensor (if we have it)
EV8612 | Magnet Reservoir Supply vlave | Normal | - | CFI60DLP | 3 | Reverse (pos gains) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | Return flow to purifiers
EV8611CD | Cooldown Valve (Magnet Annulus bottom fill) | Manual | 0 | - | - | - | - | - | - | - | - | - | - | -
PID Group: | Phase of Operation:
S3 | 4K Operation of the Solenoid
4K supercritical gas is used to cool and fill the Lead Reservoir and then liquid is withdrawn from the reservoir to cool the magnet
Device to be controlled | Description | Mode | Manual Position | Input | Set val | Reverse or Direct or interlock | Max Pos | Min Pos | Max Chg | Min Chg | Sample Time (sec) | Kp | Ki | Kd | Gain Ratio Kp/(Ki*ST) (typ~3) | Date PID Verified to work | Verifying Persons Initials | Comments
PV8522SCD | Solenoid Warm Return Valve | Manual | 0 | - | - | - | - | - | - | - | - | - | - | - | - |  |  | closed once the magnet has level in the lead reservoir
PV8522SR | Solenoid Cold Return Valve | Normal | - | PT8620 | 1.2 to 1.3 | Direct (Negative gains) | 100 | 0 | 3 | 0.2 | 10 | -30 | -1 | 0 | 3 |  |  | Use once the magnet has level in the lead reservoir
PV8512S | 4K supply to Solenoid | Manual | 100 |  |  | - | - | - | - | - | - | - | - | - | -
PV8674 | Magnet Reservoir Return Isolation Valve | Manual | 100 | - | - | - | - | - | - | - | - | - | - | - | -
EV8670BY | Shield Bypass Valve | Manual | 0 |  |  | - | - | - | - | - | - | - | - | - | -
EV8670BY | Shield Bypass Valve | Normal | - | SSHLD_DP | 0.1 | Direct (Negative gains) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
[6 empty] | - | - | - | - | - | - | - | - | - | -
EV8611JT | Lead Reservoir JT valve | Normal | - | LL8620SC | 60 | Reverse (pos gains) | 60 | from PID | 5 | 0.2 | 200 | 1.7 | 0.002 | 0 | 4.25 |  |  | Primary Liquid fill Valve for leads
EV8611JT_MIN | Lead Reservoir JT valve | Normal | - | TR8610 | 5.5 | Reverse (pos gains) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD |  |  | Min to keep U-tube from getting warm
HTR8620 | Interlock on Lead Reservoir helium level | Interlock |  | LL8620SC | 20 | - | - | - | - | - | - | - | - | - | - |  |  | Disabled if LL8620SC is below 10%
HTR8620 | Heater to boost lead flow if needed | Normal |  | PV8522SR.OVAL | 6 | - | - | - | - | - | - | - | - | - | - |  |  | turn on to keep enough flow/pressure for the current leads by keeping PV8522SR open
EV8612 | Magnet Reservoir Supply vlave | Normal | - | LL8670SC | 60 | Reverse (pos gains) | 60 | from PID | 5 | 0.2 | 200 | 1.7 | 0.002 | 0 | 4.25 |  |  | Vaporizer overpowered temperature sensor
HTR8670 | Interlock on Magmet Reservoir helium level | Interlock |  | LL8670SC | 20 | - | - | - | - | - | - | - | - | - | - |  |  | Disabled if LL8670SC is below 10%
HTR8670 | Heater to boost shield flow if needed | Normal |  | SSHLDOOUT_T_AVG | 30-80 | Direct (Negative gains) | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
EV8611CD | Cooldown Valve (Magnet Annulus bottom fill) | Manual | 0 | - | - | - | - | - | - | - | - | - | - | - | -
Note on E31: David Kashy: At present the purifiers at CHL are not working well so we don't want to over power them so we will use this sensor, in the future we should be able to use other inputs such as FI8561
Note on F31: David Kashy: Confirm value with CHL operatons prior to starting
Note on E32: David Kashy: At present the purifiers at CHL are not working well so we don't want to over power them so we will use this sensor, in the future we should be able to use other inputs such as FI8561
Note on F32: David Kashy: Confirm vlalue with CHL operations prior to starting

## Var_calcs and Intloc TH
Solenoid PID's
|  | D. Kashy - Start 10_28_2016 |  | current version | 2017-05-08 08:44
General Notes:
| 1) In most cases any valve not mentioned is expected to be closed, in some cases closed valves are listed |  | 2) Signals from Cryo to import for use as info or as inputs to our control loops: CFI6711B, EV6711B, EV6721B, EV6751, CFI082, CPI084, CT6030B, CPI603QB, CTD672, CPI8521, CTD8521
Signals needed for Cooldown Control
| Signal name | Description | Formula |  |  | Limit for Interlock and Intervention | Control Set value | NOTES | Interlock Actions (above intervention level in column G)
SolenoidPVArray[9] | COIL_T_AVG | The average of all temperature sensors on all the Coils | =Average(TS05,TS06,…,TS14) |  |  | N/A | N/A
SolenoidPVArray[10] | COIL_T_MAX | Maximum of All Temperatures Sensors on the Coils | =MAX(TS05,TS06,…,TS14)
SolenoidPVArray[11] | C14_DT_MAX | Maximum differential temperature of coils 1-4 | =MAX(TS05,TS06,…,TS12)-MIN(TS05,TS06,…,TS12) |  |  | 10K |  |  | Close PV8563C and PV8563W
SolenoidPVArray[12] | C14ASY_DT_MAX | Maximum differential temperature of coils 1-4 and Bobin and Cooling Plate | =MAX(TS01,TS02,…,TS12,TS32,TS33)-MIN(TS01,TS02,…,TS12,TS32,TS33) | [5 empty] | Close PV8563C and PV8563W
SolenoidPVArray[13] | C14ASY_DT_MAXSET |  | Entered value from Epics to the PLC |  |  | 25K
SolenoidPVArray[14] | C14ASY_DT_MAXPCT |  | =C14ASY_DT_MAX/C14ASY_DT_MAXSET * 100 |  |  |  |  | Use in comparision of max allowed DT's
SolenoidPVArray[15] | C5BOB_DT_MAX | Maximum differential temperature of any sensor on C5 and on the C5 Bobbin | =MAX( TS13, TS14, TS23,TS24) - MIN(TS13, TS14, TS23,TS24)
SolenoidPVArray[16] | C5BOB_DT_MAXSET |  |  |  |  | 20K
SolenoidPVArray[17] | C5BOB_DT_MAXPCT |  | = C5BOB_DT_MAX/C5BOB_DT_MAXSET*100
SolenoidPVArray[18] | CM_T_MAX | Max of all 4K mass temps | =MAX(TS01,TS02,…TS14, TS32,TS33)
SolenoidPVArray[19] | CM_T_MIN | Min of all 4K mass temps | =MIN(TS01,TS02,…TS14, TS32,TS33)
SolenoidPVArray[20] | CM_DT_MAX | Cold Mass Differential Temperature | CM_T_MAX-CM_T_MIN |  |  |  |  | Control Max of PV8563C to this and or Interlock supply flow to this? | Close PV8563C and PV8563W
SolenoidPVArray[21] | CM_DT_MAXSET |  | Entered value from Epics to the PLC |  |  | 40K
SolenoidPVArray[22] | CM_DT_MAXPCT |  | =CM_DT_MAX/CM_DT_MAX_Allowed * 100 |  |  |  |  | Use in comparision of max allowed DT's
| HE_CP_CD_DT |  | TR8610-TS01
SolenoidPVArray[23] | HE_METAL_CD_DT | Difference between inlet helium temp (TR8610) and helium metal temperatures {for Cooldown} | =TR8610-CM_T_MAX |  |  | -55K | -45K | This is the primary control variable for PV8653C during cooldown | Close PV8563C and PV8563W
SolenoidPVArray[24] | HE_METAL_WU_DT | Difference between inlet helium temp (TR8610) and helium metal temperatures {for Warmup} | =TR8610-CM_T_MIN |  |  | 55K | 45K | This is the primary control variable for PV8653C during warm up | Close PV8563C and PV8563W
SolenoidPVArray[25] | HE_METAL_CD_DT2 | Difference between inlet helium temp (TD8513S) and helium metal temperatures {for Cooldown} | =TD8513S-CM_T_MAX |  |  | -55K | -45K | This is an alternate control variable for PV8653C during cooldown | Close PV8563C and PV8563W
SolenoidPVArray[26] | HE_METAL_WU_DT2 | Difference between inlet helium temp (TD8513S) and helium metal temperatures {for Warmup} | =TD8513S-CM_T_MIN |  |  | 55K | 45K | This is an alternate control variable for PV8653C during warm up | Close PV8563C and PV8563W
SolenoidPVArray[27] | CP_T_MAX | Maximum Cooling plate (attached to buttons) Temperature | =MAX(TS01,TS02,TS03,TS04)
SolenoidPVArray[28] | SHLDOUT_T_MAX | Maximum of: 2 shield outlets | =MAX(TR8672,TR8673) |  |  | N/A
SolenoidPVArray[29] | SHLDOUT_T_AVG | Average of 2 shield outlets | =AVG(TR8672,TR8673)
SolenoidPVArray[30] | SHLD_T_MAX | Maximum of all temperatures sensors on the Solenoid Heat Shields | =MAX(TS28,TS29,30,31,34…41)
SolenoidPVArray[31] | SHLD_DP | Pressure Drop of the Shield | =PT8670-PT8675A |  |  |  |  | Can be used to assure we get shield flow
SolenoidPVArray[32] | HE_SHLD4K_DT | Difference between Helium inlet to shields and SSHIELD_T_MAX | =TR8670-SHLD_T_MAX |  |  | 40 | 25
| PV8563_DP_OFFSET | Amount of pressure below the 4K supply pressure to assure no mixing | Entered value from Epics to the PLC |  |  |  | 0.2-0.3 | note there was a W in this prior to 11/10 | Do we need to do it this way or delete this variable
| P_CDHE_8563W_S | Control pressure for Solenoid Cooldown or Warmup | =PT8513T-PT8565 |  |  |  |  | may need heavy filtering
| P_CDHE_8563W_T | Control pressure for Torus Cooldown or Warmup | =PT8513S-PT8565 |  |  |  |  | may need heavy filtering
SolenoidPVArray[33] | COIL_DT_Dt30 | Time rate of change of SCOIL_T_AVG over the last 30 minutes | COIL_T_AVG(now)-COIL_T_AVG(30min ago)/.5 (units K/hr) |  |  | 5 | 3
SolenoidPVArray[34] | COIL_DT_Dt120 | Time rate of change of SCOIL_T_AVG over the last 120 minutes | COIL_T_AVG(now)-COIL_T_AVG(120min ago)/2 (units K/hr) |  |  | 5 | 3
SolenoidPVArray[35] | COIL_DT_Dt600 | Time rate of change of SCOIL_T_AVG over the last 600 minutes | COIL_T_AVG(now)-COIL_T_AVG(600min ago)/10 (units K/hr) |  |  | 5 | 3
SolenoidPVArray[36] | SHLDOUT_DT_Dt30 | Time rate of change of SSHLDOUT_T_AVG over the last 30 minutes | SHLDOUT_T_AVG(now)-SHLDOUT_T_AVG(30min ago)/.5 (units K/hr) |  |  | 5 | 3
SolenoidPVArray[37] | SHLDOUT_DT_Dt120 | Time rate of change of SSHLDOUT_T_AVG over the last 120 minutes | SHLDOUT_T_AVG(now)-SHLDOUT_T_AVG(120min ago)/2 (units K/hr) |  |  | 5 | 3
SolenoidPVArray[38] | SHLDOUT_DT_Dt600 | Time rate of change of SSHLDOUT_T_AVG over the last 600 minutes | SHLDOUT_T_AVG(now)-SHLDOUT_T_AVG(600min ago)/10 (units K/hr) |  |  | 5 | 3
| SLR_CD_DT | Control temperature difference for the lead reservoir | TD8513S-TD8522SR |  |  |  | -10 | This will allow controlling PV8566S to get a trickle flow to the Lead Reservoir through w/o wasting cooling power
SolenoidPVArray[39] | SSHLD_CD_DT | Control temperature difference for the solenoid shields | TD8513S-AVG(TR8672,TR8673) |  |  |  |  | This will allow controlling EV8670BY so that the shields are not completely bypassed and stay warm
SolenoidPVArray[40] | SSHLD_DT_MAX | Temperature difference between warmest and coldest part of magnet shield | MAX(TS28,TS29,TS30,31,34,35,…,TS41)-MIN(TS28,TS29,TS30,31,34,35,…,TS41) |  |  |  |  | A way to easily check the thermal gradient in the shields. Is there a limit??
SolenoidPVArray[41] | SSHLD_4K_DT_MAX | Maximum difference 4K and Shield temperatures | MAX(TS01,TS02,…TS14, TS28,TS29,…,TS41)- MIN(TS01,TS02,…TS14, TS28,TS29,…,TS41) |  |  |  |  | Full limit of DT across the Shield and the Magnet
SolenoidPVArray[42] | SSHLD_4K_DT_MAX_Allowed |  | Entered value from Epics to the PLC |  |  | 50K
SolenoidPVArray[43] | SSHLD_4K_DT_MAX_Percent |  | =SHLD4K_DT_MAX/SHLD4K_DT_MAX_Allowed * 100 |  |  |  |  | Use in comparision of max allowed DT's
SolenoidPVArray[44] | S_DT_MAX_Percent |  | =MAX( SHLD4K_DT_MAXPCT, CM_DT_MAXPCT,C14ASY_DT_MAXPCT ,C5BOB_DT_MAXPCT) |  |  | 100 |  | Use as interlock for PV8563C and PV8563W to close, May also be used to control Flow or mix temperature
N/A
| HTR8620 | Lead Reservoir Heater | N/A |  |  | 20 |  |  | Heater will be disabled if LL8620SC is below 20%
| HTR8672 | Magnet Thermosiphon Flow Heater | N/A |  |  | 20 |  |  | Heater will be disabled if LL8670SC is below 20%
| Axial and Radial load cell interlocks | In a separate document
| ETI Name | ETI Description | JLab Name
| TS 01 | He channel Cu plate - Inlet (6-oclock) | TR86101CP_B |  | CX-1050-CU-HT-1.4L
| TS 02 | He channel Cu plate - Inlet (6-oclock) | TR86102CP_B |  | CX-1050-CU-HT-1.4L | KEY
| TS 03 | He channel Cu plate - outlet (12-oclock) | TR86103CP_T |  | CX-1050-CU-HT-1.4L | CP | Cooling Plate
| TS 04 | He channel Cu plate - outlet (12-oclock) | TR86104CP_T |  | CX-1050-CU-HT-1.4L | B | Bottom
| TS 05 | C1 Coil ID - 12-oclock | TR86105C1 |  | CX-1050-SD-HT-1.4L | T | Top
| TS 06 | C1 Coil ID - 12-oclock | TR86106C1 |  | CX-1050-SD-HT-1.4L | C1 | Coil 1
| TS 07 | C2 Coil ID - 12-oclock | TR86107C2 |  | CX-1050-SD-HT-1.4L | C2 | Coil 2
| TS 08 | C2 Coil ID - 12-oclock | TR86108C2 |  | CX-1050-SD-HT-1.4L | C3 | Coil 3
| TS 09 | C3 Coil OD - 12-oclock | TR86109C3 |  | CX-1050-SD-HT-1.4L | C4 | Coil 4
| TS 10 | C3 Coil OD - 12-oclock | TR86110C3 |  | CX-1050-SD-HT-1.4L | C5 | Coil 5
| TS 11 | C4 Coil OD - 12-oclock | TR86111C4 |  | CX-1050-SD-HT-1.4L | SP | Splice
| TS 12 | C4 Coil OD - 12-oclock | TR86112C4 |  | CX-1050-SD-HT-1.4L | RS | Radial Support (really tangential)
| TS 13 | C5 Coil OD - 12-oclock | TR86113C5 |  | CX-1050-SD-HT-1.4L | US | Upstream
| TS 14 | C5 Coil OD - 12-oclock | TR86114C5 |  | CX-1050-SD-HT-1.4L | DS | Downstream
| TS 15 | C1-C3 Lead splice - 12-oclock | TR86115SP_C1_C3 |  | CX-1050-SD-HT-1.4L | C | Cold
| TS 16 | C1-C3 Lead splice - 12-oclock | TR86116SP_C1_C3 |  | CX-1050-SD-HT-1.4L | M | Midway
| TS 17 | C3-C5 Lead splice - 12-oclock | TR86117SP_C3_C5 |  | CX-1050-SD-HT-1.4L | HS | Heat Shield
| TS 18 | C3-C5 Lead splice - 12-oclock | TR86118SP_C3_C5 |  | CX-1050-SD-HT-1.4L | BO | Bore
| TS 19 | C5-C4 Lead splice - 12-oclock | TR86119SP_C4_C5 |  | CX-1050-SD-HT-1.4L | OD | Outside Diameter
| TS 20 | C5-C4 Lead splice - 12-oclock | TR86120SP_C4_C5 |  | CX-1050-SD-HT-1.4L | BOB | C1-4 SST Bobin
| TS 21 | C4-C2 Lead splice - 12-oclock | TR86120SP_C2_C4 |  | CX-1050-SD-HT-1.4L | LBR | Lower Beam Right
| TS 22 | C4-C2 Lead splice - 12-oclock | TR86121SP_C2_C4 |  | CX-1050-SD-HT-1.4L | UBR | Upper Beam Right
| TS 23 | Upstream C5 - 10-oclock (C5 Bobbin) | TR86123RS_US_T_BL_C |  | CX-1050-CU-HT-1.4L | LBL | Lower Beam Left
| TS 24 | Dnstream C5 - 8-oclock (C5 Bobbin) | TR86124RS_DS_B_BL_C |  | CX-1050-CU-HT-1.4L | UBL | Upper Beam Left
| TS 25 | Upstream link - 10-oclock | TP86125RS_US_T_BL_M |  | PT-102-AL-14L | ZS | Z-Support
| TS 26 | Upstream link - 10-oclock | TP86126RS_US_T_BL_M |  | PT-102-AL-14L
| TS 27 | Dnstream link - 8-oclock | TP86127RS_DS_B_BL_M |  | PT-102-AL-14L
| TS 28 | RADShield ID - 6-oclock | TP86128HS_BO_B_BR |  | PT-102-AL-14L | is this on the beam right or left side?
| TS 29 | RADShield ID - 6-oclock | TP86129HS_BO_B_BL |  | PT-102-AL-14L | is this on the beam right or left side?
| TS 30 | RADShield OD - 6-oclock | TP86130HS_B_OD |  | PT-102-AL-14L
| TS 31 | RADShield OD - 6-oclock | TP86131HS_B_OD |  | PT-102-AL-14L
| TS 32 | C1-4 Bobbin OD - 12 oclock | TR86132BOB_US |  | CX-1050-CU-HT-1.4L
| TS 33 | C1-4 Bobbin OD - 12 oclock | TR86133BOB_DS |  | CX-1050-CU-HT-1.4L
| TS 34 | RADShield Upstrm Cone - 4-oclock | TP86134HS_US_CO_LBR |  | PT-102-AL-14L |  |  |  |  | is this view looking Downstream?
| TS 35 | RADShield Dnstrm Cone - 4-oclock | TP86135HS_DS_CO_LBR |  | PT-102-AL-14L |  |  |  |  | that will tell us if TS28 is BR or BL
| TS 36 | RADShield Upstrm Cone - 2-oclock | TP86136HS_US_CO_UBR |  | PT-102-AL-14L
| TS 37 | RADShield Dnstrm Cone - 2-oclock | TP86137HS_DS_CO_UBR |  | PT-102-AL-14L
| TS 38 | RADShield Upstrm Cone - 10-oclock | TP86138HS_US_CO_UBL |  | PT-102-AL-14L
| TS 39 | RADShield Dnstrm Cone - 10-oclock | TP86139HS_DS_CO_UBL |  | PT-102-AL-14L
| TS 40 | RADShield Upstrm Cone - 8-oclock | TP86140HS_DS_CO_LBL |  | PT-102-AL-14L
| TS 41 | RADShield Dnstrm Cone - 8-oclock | TP86141HS_US_CO_LBL |  | PT-102-AL-14L
CX-1050-CU-HT-1.4L
CX-1050-SD-HT-1.4L
PT-102-AL-14L
| AL01 | Axial Load Cell Upstream - 4-oclock | ZS86101US_BR_B
| AL02 | Axial Load Cell Dnstream - 4-oclock | ZS86102DS_BR_B
| AL03 | Axial Load Cell Dnstream - 2-oclock | ZS86103DS_BR_T
| AL04 | Axial Load Cell Upstream - 2-oclock | ZS86104US_BR_T
| AL05 | Axial Load Cell Upstream - 10-oclock | ZS86105US_BL_T
| AL06 | Axial Load Cell Dnstream - 10-oclock | ZS86106DS_BL_T
| AL07 | Axial Load Cell Dnstream - 8-oclock | ZS86107DS_BL_B
| AL08 | Axial Load Cell Upstream - 8-oclock | ZS86108US_BL_B
| RL01 | Radial Load Cell Upstream - 4-oclock | RS86101US_BR_B
| RL02 | Radial Load Cell Dnstream - 4-oclock | RS86102DS_BR_B
| RL03 | Radial Load Cell Dnstream - 2-oclock | RS86103DS_BR_T
| RL04 | Radial Load Cell Upstream - 2-oclock | RS86104US_BR_T
| RL05 | Radial Load Cell Upstream - 10-oclock | RS86105US_BL_T
| RL06 | Radial Load Cell Dnstream - 10-oclock | RS86106DS_BL_T
| RL07 | Radial Load Cell Dnstream - 8-oclock | RS86107DS_BL_B
| RL08 | Radial Load Cell Upstream - 8-oclock | RS86108US_BL_B

## SST Interlocks
Task | Solenoid Interlock
Engineer | D. Kashy and Renuka Rajput-Ghoshal
Date | December 16th 2016
Version | 1
Signal Name | Description | Units | Normal Range | Fast Ramp (Hardwire) | Fast Dump (PLC) | Controlled Ramp (PLC) (2A/sec) | Delay Threshold | Notes
LL8620DP | Helium Level | % | 70-80 | N/A | N/A | <40 | 1s | Low level means conductor in SST would go dry
LL8620SC | Helium Level | % | 70-80 | <20 | N/A | <40 | 1s | Low level means conductor in SST would go dry
LL8670DP | Helium Level | % | 70-80 | N/A | N/A | <60 | 1s
LL8670SC | Helium Level | % | 70-80 | <20 | N/A | <30 | 1s
PT8620 | Helium Tank Pressure | atm | 1.1-1.3 | N/A | N/A | >1.6 | 3s | Higher pressure means higher lead temps
PT8670 | Helium Tank Pressure | atm | 0.5-1.2 | N/A | TBD | TBD | TBD | Higher pressure means higher coil temps
TD8622A&B | VCL Temperatures | K | 5-10 | >15? | >14 | >12 | 400ms | may need to be raised, why not just use voltage drop?
FV8621A&B | VCL Flow | SLM | 35.4-41.3 | N/A | N/A | +/- 5SLPM of SP | 500ms
TD8624A&B | Splice Temperature | K | 4.5-5 | >8.5 |  |  | 400ms | may need to be raised, why not just use voltage drop?
VT1_DAQ&VT19_DAQ | VCL Voltage Drop | mV | 0-10 | >100 | >80 | >50 | 650ms
Comparators 1 & 2 | Coil/Splice Voltage Drop | mV | 0 | >60 | 100 | 80 | 1s(controlled), 650ms(Fast
| Chassis Watchdog | sec | 0 | >5 | N/A | N/A
| Current lead water flow Supply | gpm | ? | <3.4 | N/A | N/A |  | Why are the values differernt???
| Current lead water flow return | gpm | ? | <3.2 | N/A | N/A |  | Why are the values differernt???
TP8621A&B | Current Lead Temp | K | ~300 | N/A | N/A | 350 | N/A
| VT cable connector disconnected |  | N/A | Any disconnect | N/A | N/A
| Coil and HB cable connector disconnected |  | N/A | Any disconnect
| Fast Dump Button (EPICs GUI) |  | N/A |  | push button
| Current Limit (Hard coded) |  | 0-2416 |  | 2450
| VESDA Fire Detection |  |  | N/A | N/A | on/off
| UPS Battery low |  |  | N/A | N/A | on/off
PV8522SCD | Cooldown Valve (warm return) | [6 empty] | Future could open on Quench or FD
PV8522SR | Cold return Valve | [6 empty] | Future could close on Quench or FD
SV8622 | Lead flow to atmosphere vent |  |  | open | open | closed |  | opens above 80mV on lead voltage drop, closed when voltage drop falls below 60mV
Note on G14: Renuka Rajput-Ghoshal: This is 15 for Torus.
Note on G17: Renuka Rajput-Ghoshal: This may not be required