## Sheet1
Date: 5/8/2017
Solenoid SOE - Test Checkout
Relay Number | Event Checked | Hardware Relay | PLC SOE Module |  | MPS Dump Switch Open | EPICS - Interlock Status Screen | Coments
|  |  | Hardware- SOE Module Indicator Display | Software-PLC readout Indicator status
0 | Lead Temperature | ü | û | ü | ü | û | Assigned indicator does not change status on EPICS screen
1 | Liquid Helium Level 8620SC | ü | û | ü | ü | û | Assigned indicator does not change status on EPICS screen
2 | Liquid Helium Level 8670SC | ü | û | ü | ü | û | Assigned indicator does not change status on EPICS screen
3 | Crycon 1 | ü | û | ü | ü
4 | Crycon 2 | ü | û | ü | ü
5 | Spare | Not tested | Not tested | Not tested | Not tested | Not tested
6 | PLC Fast Dump | ü | û | ü | ü | ü
7 | Vacuum SUM Interlock | ü | û | ü | ü
8 | Watchdog | ü | ü | ü | ü | ü
9 | Current Lead Water Flow
| Supply Switch | ü | ü | ü | ü | ü | Set at 3.2 [GPM]
| Return Switch | ü | ü | ü | ü | ü | Set at 3.4 [GPM]
10 | VT Cable Intrerlock | Not tested | Not tested | Not tested | Not tested | Not tested | Cable - waiting to be connected to the Solenoid
11 | System Cable Interlock | Not tested | Not tested | Not tested | Not tested | Not tested | Cable - waiting to be connected to the Solenoid
12 | Quench Detector 1
| Channel 1 | ü | ü | ü | ü | ü | Threshold Set = 60 [mV]/ Tripped at 64 [mV]
| Channel 2 | ü | ü | ü | ü | ü | Threshold Set = 60 [mV]/ Tripped at 62 [mV]
| Channel 3 | ü | ü | ü | ü | ü | Threshold Set = 100 [mV]/ Tripped at 100 [mV]
| Channel 4 | ü | ü | ü | ü | ü | Threshold Set= 100 [mV]/ Tripped at 101[mV]
13 | Quench Detector 2
| Channel 5 | ü | ü | ü | ü | ü | Threshold Set = 100 [mV]/ Tripped at 100 [mV]
| Channel 6 | ü | ü | ü | ü | ü | Threshold Set = 100 [mV]/ Tripped at 102 [mV]
| Channel 7 | ü | ü | ü | ü | ü | Threshold Set = 60 [mV]/ Tripped at 62 [mV]
| Channel 8 | ü | ü | ü | ü | ü | Threshold Set = 60 [mV]/ Tripped at 62 [mV]
14 | Spare | ü | ü | Not tested | Not tested | Not tested
15 | Spare | ü | ü | Not tested | Not tested | Not tested