## Solenoid Drawings List
2017-05-15
Drawing Number | Drawing Name | REV - | REV A | NOTES:
B00000-09-00-0600 | Solenoid Cryogenics P & I Diagram | IN WORK
B00000-09-00-0605 | Drawing List
B00000-09-00-0610 | System Overview
B00000-09-00-0611 | Rack Layout | COMPLETE
B00000-09-00-0612
B00000-09-00-0613
B00000-09-00-0614
B00000-09-00-0615 | Ethernet Single Line | UNDEFINED
B00000-09-00-0616 | Serial Single Line | UNDEFINED
B00000-09-00-0617
B00000-09-00-0618
B00000-09-00-0619
B00000-09-00-0620 | Local Backpanel Assembly | COMPLETE
B00000-09-00-0621 | Local 24 VDC Power Source | COMPLETE
B00000-09-00-0622 | Local PLC Chassis Assembly | COMPLETE
B00000-09-00-0623 | Local Slot 1 - | COMPLETE
B00000-09-00-0624 | Local Slot 2 - | COMPLETE
B00000-09-00-0625 | Local Slot 3 - |  |  | PLACEHOLDER
B00000-09-00-0626 | Local Slot 4 - | COMPLETE
B00000-09-00-0627 | Local Slot 5 - | COMPLETE
B00000-09-00-0628 | Local Slot 6 - | COMPLETE
B00000-09-00-0629 | Local Slot 7 - |  |  | PLACEHOLDER
B00000-09-00-0630 | Local Slot 8 - | WEB+ |  | PLACEHOLDER
B00000-09-00-0631 | Local Slot 9 - | ETHERNET |  | PLACEHOLDER
B00000-09-00-0632
B00000-09-00-0633 | VT ISOAMP Sub-chassis (Machanical)
B00000-09-00-0634
B00000-09-00-0635 | Remote Backpanel Assembly | COMPLETE
B00000-09-00-0636 | Remote PLC Chassis Assembly | COMPLETE
B00000-09-00-0637 | Remote 24 VDC Power Source | COMPLETE
B00000-09-00-0638 | Remote Slot 0 - | COMPLETE
B00000-09-00-0639 | Remote Slot 1 - | COMPLETE
B00000-09-00-0640 | Remote Slot 2 - | COMPLETE
B00000-09-00-0641 | Remote Slot 3 - | COMPLETE |  | PLACEHOLDER
B00000-09-00-0642 | Remote Slot 4 - | COMPLETE
B00000-09-00-0643 | Remote Slot 5 - | COMPLETE
B00000-09-00-0644 | Remote Slot 6 - |  |  | PLACEHOLDER
B00000-09-00-0645 | Remote Slot 7 - | COMPLETE
B00000-09-00-0646 | Remote Slot 8 - |  |  | PLACEHOLDER
B00000-09-00-0647 | Remote Slot 9 - | ETHERNET |  | PLACEHOLDER
B00000-09-00-0648 | Interconnect Panel Layout | COMPLETE
B00000-09-00-0649 | CRYOCON Termination & SOE Detail | COMPLETE
B00000-09-00-0650 | EV Relays (Sht 1 & 2) | COMPLETE
B00000-09-00-0651 | LVDT's | COMPLETE
B00000-09-00-0652 | EV & LVDT Cables | COMPLETE
B00000-09-00-0653 | Keep Alive Timing Relay Wiring | COMPLETE
B00000-09-00-0654 | Magnet Power Supply Connections | COMPLETE
B00000-09-00-0655 | Vacuum Controls Layout | COMPLETE | COMPLETE
B00000-09-00-0656 | Vacuum Interlock & Control Schematic | COMPLETE | COMPLETE
B00000-09-00-0657 | Vacuum Switch Panel Layout | COMPLETE | COMPLETE
B00000-09-00-0658 | Vacuum Turbo Control Panel Layout | COMPLETE
B00000-09-00-0659 | LHe & LN2 Liquid Level/DP Wiring | COMPLETE
B00000-09-00-0660 | Mass Flow Measurement | COMPLETE
B00000-09-00-0661 | Immersion Heater Wiring_8672/8601 | COMPLETE
B00000-09-00-0662 | Force Washer Load Cells | COMPLETE
B00000-09-00-0663 | Immersion Heater Wiring_8620/8623 | COMPLETE
B00000-09-00-0664 | Magnet Relief Sensor Wiring Diagrams | COMPLETE
B00000-09-00-0665 | Solenoid Sensor Wiring Diagrams #1 | COMPLETE
B00000-09-00-0666 | Solenoid Sensor Wiring Diagrams #2 | COMPLETE
B00000-09-00-0667 | Solenoid Sensor Wiring Diagrams #3 | COMPLETE
B00000-09-00-0668 | Solenoid Sensor Wiring Diagrams #4 | COMPLETE
B00000-09-00-0669 | Solenoid Sensor Wiring Diagrams #5 | COMPLETE
B00000-09-00-0670
B00000-09-00-0671
B00000-09-00-0672
B00000-09-00-0673
B00000-09-00-0674
B00000-09-00-0675
B00000-09-00-0676
B00000-09-00-0677 | Spares Sensor Wiring Diagrams | COMPLETE
B00000-09-00-0678 | Chimney Wiring & CRYOCONS | COMPLETE
B00000-09-00-0679 | VT Attenuator 24 VDC Power | COMPLETE
B00000-09-00-0680 | Voltage Tap System Diagram | COMPLETE
B00000-09-00-0681 | Voltage Tap Backpanel | COMPLETE
B00000-09-00-0682 | cRIO Sub-Chassis (Mechanical) | COMPLETE
B00000-09-00-0683 | VT Attenuator sub-chassis | COMPLETE
B00000-09-00-0684 | Voltage Tap Test Panel Assembly | COMPLETE
B00000-09-00-0685 | Voltage Tap Test Panel Mechanical | COMPLETE
B00000-09-00-0686 | Voltage Tap Test Panel Electrical | COMPLETE
B00000-09-00-0687 | Quench Detector Wiring | COMPLETE
B00000-09-00-0688 | cRIO RS-232 Wiring Detail | COMPLETE
B00000-09-00-0689 | cRIO 24VDC Wiring Drawing | COMPLETE
B00000-09-00-0690 | Resisitor Chassis Layout Mechanical | IN WORK
B00000-09-00-0691 | Resisitor Chassis Connector Panel | COMPLETE |  | MACHINE SHOP
B00000-09-00-0692
B00000-09-00-0693
B00000-09-00-0694 | Small Resistor Board (2) | IN WORK
B00000-09-00-0695 | Large Resistor Board (2) | IN WORK
B00000-09-00-0696
B00000-09-00-0697
B00000-09-00-0698
B00000-09-00-0699 | Ice Management Controls Panel | COMPLETE |  | MACHINE SHOP

## Solenoid Signal I.D.'s
ID | Location | Type | 4-20 mA IN | Voltage IN | Digital IN (Sinking) | Digital IN (Sourcing) | 4-20 mA OUT | Voltage OUT | Relay OUT | 4-20mA OUT | Cryocon/LakeShore (NBX) | Serial Connection (NBX) | Pressure Indicator | # of Cables | # wires | Notes | Signal Type | INTERNAL Wiring Map Complete | EXTERNAL Wiring Map Complete | Cable Map (Definition) Complete | Schematic Diagram Complete
TEMPERATURE (CERNOX)
ID | Location | Type | [12 empty] | # wires | Notes
TR8611 | Cooldown Helium Supply Temp | Temperature (Cernox) | [8 empty] | 1 |  |  |  |  | +redundant | Cryocon/Ethernet
TR8622A | Lead A Top | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8622B | Lead B Top | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8624A | Lead A Bottom | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8624B | Lead B Bottom | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8670 | Lhe Tank Vent (pre-valve) | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8671 | Magnet Reservoir Return | Temperature (Cernox) | [8 empty] | 1 |  |  |  |  | +redundant | Cryocon/Ethernet
TR8672 | Shield Supply | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8673 | Shield Vent | Temperature (Cernox) | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TR8674 | Lhe Tank Vent | Temperature (Cernox) | [8 empty] | 1 |  |  | 1 | 8 | +redundant | Cryocon/Ethernet
TR8610 |  | Temperature (Cernox) | [8 empty] | 1 |  |  | 1 | 8 | +redundant | Cryocon/Ethernet
TEMPERATURE (PT100)
ID | Location | Type | [12 empty] | # wires | Notes
TP8621A | Lead A Warm End | PT100 | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TP8621B | Lead B Warm End | PT100 | [8 empty] | 1 |  |  | 1 | 8 | +redundant | Cryocon/Ethernet
TP8675 | LHE Return Line Temp (outside can) | PT100 | [8 empty] | 1
TP8676A | LHE Return Line Temp (outside can) | PT100 | [8 empty] | 1 |  |  |  | 8 | +redundant | Cryocon/Ethernet
TP8676B | LHE Return Line Temp (outside can) | PT100 | [8 empty] | 1
TP8677 | LHE Return Line (after pumps) | PT100 | [8 empty] | 1 |  |  | 1 | 8 | +redundant | Cryocon/Ethernet
PRESSURE
ID | Location | Type | [12 empty] | # wires | Notes
PT8620 | Lead Reservoir Pressure | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
PT8670 | Magnet Reservoir Pressure | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
PT8675A | LHE Return Line Press | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
PT8675B | LHE Return Line Press Sub-ATM | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
PT8677 | Inlet to guard vacuum | Pressure | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
LL8620DP | Lead Reservoir dP LL | dP | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
LL8670DP | Magnet Reservoir dP LL | dP | 1 | [10 empty] | 1 | 2 |  | 4-20 mA
TC8600 | Vacuum | Vacuum TC |  | 1 | [9 empty] | 1 | 2
LIQUID LEVEL
ID | Location | Type | [12 empty] | # wires | Notes
LL8620SC | Lead Reservoir LL | Superconducting Probe |  | 1 | [9 empty] | 1 |  |  | 0-10V
LL8670SC | Magnet Reservoir LL | Superconducting Probe |  | 1 | [9 empty] | 1 |  |  | 0-10V
VALVES
ID | Location | Type | [12 empty] | # wires | Notes | [5 empty] | Added
EV8611CD | Cooldown Bottom Fill | EV | [6 empty] | 2 |  |  |  |  | 2 | 2 | 2 x relay out | 24 VDC
EV8670BY | Lhe Return Valve | EV | [6 empty] | 2 |  |  |  |  | 2 |  | 2 x relay out | 24 VDC
EV8611JT | Top Fill | EV | [6 empty] | 2 |  |  |  |  | 2 | 2 | 2 x relay out | 24 VDC
EV8612 | Bottom Fill | EV | [6 empty] | 2 |  |  |  |  | 2 | 5 | 2 x relay out | 24 VDC
EV8611CD_LVDT | Cooldown Bottom Fill | EV | 1 | [10 empty] | 2 | 2 | LVDT analog in | 4-20 mA
EV8670BY_LVDT | Lhe Return Valve | EV | 1 | [10 empty] | 2 |  | LVDT analog in | 4-20 mA
EV8611JT_LVDT | Top Fill | EV | 1 | [10 empty] | 2 | 2 | LVDT analog in | 4-20 mA
EV8612_LVDT | Bottom Fill | EV | 1 | [10 empty] | 2 | 5 | LVDT analog in | 4-20 mA
PV8674 | Warm Return Valve | PV | [6 empty] | 1 | [6 empty] | Pnumatic Sealed Bellows | 4-20 mA
SV8622 | Lead Flow Vent to Atmosphere | Solenoid | [6 empty] | 1
SV8678CR | Warm Return Valve | Solenoid | [6 empty] | 1
SV8678DV | Warm Return Vent to Atmosphere | Solenoid | [6 empty] | 1
FI/EV 8621A | Lead A Flow Control | Analog in/out | 1 |  |  |  | 1 | [6 empty] | 1
FI/EV 8621B | Lead B Flow Control | Analog in/out | 1 |  |  |  | 1 | [6 empty] | 1
PV8674 | BELLOWS SEALED VALVE | Solenoid Valve | [6 empty] | 1 | [6 empty] | relay out | 24 V
SV8675BY | Return Flow to Quench header | Solenoid Valve | [6 empty] | 1 | [6 empty] | relay out | 24 V
HEATER
ID | Location | Type | [12 empty] | # wires | Notes
HT8621A | Lead A flag heater | Heater |  |  |  |  | 1 |  | 1
HT8621B | Lead B flag heater | Heater |  |  |  |  | 1 |  | 1
HTR8620 | Lead Reservoir (2 x 20 W) | Heater |  |  | 1 |  | 1 |  | 1 |  |  |  |  | 2 |  |  | Relay Out, Analogs Out, Digital IN
HTR8672 | Mag Reservoir Return (3 x 20 W) | Heater |  |  | 1 |  | 1 |  | 1 |  |  |  |  | 2 |  |  | Relay Out, Analogs Out, Digital IN
PRESSURE INDICATOR
ID | Location | Type | [12 empty] | # wires | Notes
PIXXXXX | Relief Valve Vacuum | ???? | [10 empty] | 1 |  |  | See zone G4 near guard vac
SYSTEM HEALTH
ID | Location | Type | [12 empty] | # wires | Notes
| 24 VDC OK | Digital |  |  | 3 | [8 empty] | 1 | 2 | internal wiring | Discrete IN
| UPS Low Power | Digital |  |  | 1 | [8 empty] | 1 | 2 | internal wiring | Discrete IN
| UPS on Battery | Digital |  |  | 1 | [8 empty] | 1 | 2 | internal wiring | Discrete IN
| Vacuum pump 1 speed | Analog |  | 1
| Vacuum pump 2 speed | Analog |  | 1
| Vacuum pump 1 ON | Digital | [6 empty] | 1
| Vacuum pump 2 ON | Digital | [6 empty] | 1
Magnet Monitoring/Control
ID | Location | Type | [12 empty] | # wires | Notes
| Fast Dump | Digital | [6 empty] | 1 | [5 empty] | 2 | internal wiring | Discrete IN
| Slow Dump | Digital | [6 empty] | 1 | [5 empty] | 2 | internal wiring | Discrete IN
| Power Supply Communications | Digital | [9 empty] | 1 |  |  | 2 | internal wiring | Discrete IN
| Quench Detector Status | Digital |  |  |  | 12
| Quench Detector Reset | Digital | [6 empty] | 1
| Power Supply Resets | Digital | [6 empty] | 3
| Watchdog/Keep Alive + Reset | Digital | [6 empty] | 2
| Power Supply Status | Digital |  |  | 6 | [9 empty] | 2 | internal wiring | Discrete IN
VFD's
ID | Location | Type | [12 empty] | # wires | Notes
MP8676A | Helium vacuum pallet | Mix | 1 |  | 1 |  | 1 |  | 1 | [6 empty] | Guess? | Mixed
MP8676B | Helium vacuum pallet | Mix | 1 |  | 1 |  | 1 |  | 1 |  |  |  |  | 1 | 2 | Guess? | Mixed
Vacuun Signals
ID | Location | Type | [19 empty] | Added
CG8606 | Mid level SST Vaccum gauge |  |  | 1 | [9 empty] | 40 |  | Analog Input | 0 -10V
CG8600TB | Extension on Turbo pump side |  |  | 1 | [11 empty] | Analog Input | 0 -10V
TB8600 (TURBO) | Speed Turbo Pump Vaccum at SST |  |  | 1 | [11 empty] | Analog Input | 0 -10V
|  | TOTALS | 15 | 8 | 15 | 12 | 8 | 0 | 30 | 0 | 9 | 1 | 1
IO Required
|  | Analog IN Channels (current) | 15
|  | Analog IN Channels (voltage) | 8
|  | Analog OUT Channels | 8
|  | Relay OUT Channels | 30
|  | Digital IN Channels (Sink) | 15
|  | Digital IN Channels (Source) | 12
|  | Cryocon/LakeShore | 9
|  | Enet NBX | 1
|  | Enet RS232 | 1
|  | PLC Equip Required |  |  | Spare Channels
|  | Analog Output | 2 |  | 8 | [10 empty] | TBNH | 2
|  | Analog Input (current in) | 2 |  | 17 | [10 empty] | TBCH | 9
|  | Analog Input (voltage in) | 1 |  | 8
|  | Relay Output | 3 |  | 18
|  | Digital Input (Sinking) | 1 |  | 17
|  | Digital Input (Sourcing) | 1 |  | 20
|  | SOE Module | 1
|  | L73 Processor | 1
|  | Ethernet Module | 2 |  |  |  |  | **this becomes 2 w/ remote chassis
|  | EWEB Module | 1
|  | Total Modules | 15
|  | PLC chassis (10 slot) | 2
|  | PLC Power Supply | 2
|  | Slot Filler | 5

## Solenoid Slow Controls
SOLENOID
| Summary | 2015-10-23
Rack Hardware & Infrastructure
| PLC Hardware | 25371.56
| Valve Control/Readback | 5396
| Temperature Monitoring | 5890
| Liquid Level | 4670
| Ethernet Communications | 5000
| Local HMI | 1290
| Rack Infrastructure | 9907.2
| External Cables | 15000
| Heater Control | 4551.38
| PLC Communications | 715
| Total Solenoid SLOW Controls Hardware | 77076.14
No. | Item | Mfg | PN | Qty | Vendor | Quote Unit Price | Total Est. Price | Date Ordered | Date Expected | PR# | Total Acutal Price | Location | NOTES:
PLC Hardware
1 | 10-Slot Chassis | Allen Bradley | 1756-A10 | 2 | EECO | 478.04 | 956.08
2 | Power Supply | Allen Bradley | 1756-PA72 | 2 | EECO | 708.18 | 1416.36
3 | PLC | Allen Bradley | 1756-L72 | 1 | EECO | 5964.4 | 5964.4
4 | Ethernet Module | Allen Bradley | 1756-EN2T | 2 | EECO | 2123.8 | 4247.6
5 | Ethernet Gateway | Allen Bradley | 1756-EWEB | 1 | EECO | 2331 | 2331 | [5 empty] | May not be necessary
6 | Digital Relay Output Module (16 Ch) | Allen Bradley | 1756-OW16I | 3 | EECO | 485.44 | 1456.32
7 | Analog Input Module (16 Ch.) | Allen Bradley | 1756-IF16 | 3 | EECO | 1206.2 | 3618.6
8 | Digital Input Module, 24 VDC Sink | Allen Bradley | 1756-IB32 | 1 | EECO | 396.26 | 396.26 | [5 empty] | Estimated Price
9 | Digital Input Module, 24 VDC Source | Allen Bradley | 1756-IV32 | 1 | EECO | 396.26 | 396.26 | [5 empty] | Estimated Price
10 | Sequence of Events Module | Allen Bradley | 1756-IB16ISOE | 1 | EECO | 664.52 | 664.52
11 | Analog Output Module (8 ch) | Allen Bradley | 1756-OF8 | 2 | EECO | 1554 | 3108
12 | Module Terminal Block (16 ch) | Allen Bradley | 1756-TBCH | 9 | EECO | 65.12 | 586.08
13 | Module Terminal Block (8 ch) | Allen Bradley | 1756-TBNH | 2 | EECO | 52.54 | 105.08
14 | Slot Filler | Allen Bradley | 1756-N2 | 5 | EECO | 25 | 125 | [5 empty] | Estimated Price
[5 empty] | PLC SUBTOTAL |  | 25371.56
Valve Actuation
15 | LVDT Excitation/Readback | Macro Sensors | LVC-2500 | 4 | Macro Sensors | 571 | 2284 | [6 empty] | x
16 | Relay | Finder | 44.62.7.024.4000 | 8 |  | 3 | 24 | [5 empty] | Price guess | x
17 | Relay Base | Finder | 95.75 | 8 |  | 3 | 24 | [5 empty] | Price guess | x
18 | Relay Diode | Finder | 99.01 | 8 |  | 8 | 64 | [5 empty] | Price guess | x
19 | Mass Flow Controller Head Unit | Teledyne Hastings | Power400 | 0 |  | 2000 | 0 | [5 empty] | Price guess
20 | Mass Flow Controller | Teledyne Hastings |  | 2 |  | 1500 | 3000 | [5 empty] | Price guess
[5 empty] | VALVE SUBTOTAL |  | 5396
Temperature Monitoring
21 | TCP to Ethernet/IP | Real Time Automation | 490-NBX | 1 | Real Time Automation | 715 | 715 | [5 empty] | Could also be 460ETCTCP (does parsing), same price | x
22 | CryoCon Temperature Monitor (8 ch) | CryoCon | 18C | 3 | CryoCon | 1695 | 5085 | [6 empty] | x
23 | CryoCon Panel Mount Kit | CryoCon | 3014-020 | 3 | CryoCon | 30 | 90 | [6 empty] | x
[5 empty] | TEMPERATURE SUBTOTAL |  | 5890
Liquid Level
52 | AMI Liquid Level Monitor | AMI |  | 2 | AMI | 835 | 1670
53 | AMI Liquid Level Probe | AMI |  | 2 | AMI | 1500 | 3000
[5 empty] | LIQUID LEVEL SUBTOTAL |  | 4670
Ethernet Communications
1 | Ethernet Switch | Cisco |  | 1 |  | 5000 | 5000 | [5 empty] | Based on Hall D's Ethernet Switch
[5 empty] | ETHERNET SUBTOTAL |  | 5000
Local HMI
1 | 10" Touch Panel (Local Control Panel) | Automation Direct | EA9-T10CL | 1 | Automation Direct | 1290 | 1290 | [6 empty] | x
[5 empty] | HMI SUBTOTAL |  | 1290
Rack Infrastructure
1 | Rack | - | - | 2 | 0 | 0 | 0 | N/A |  | N/A |  | Hall B | Already on hand
2 | Back Panel |  |  | 3 |  | 200 | 600 | [6 empty] | x
22 | 24 VDC Power Supply | RHINO | PSM24-360S | 4 | Automation Direct | 229 | 916 | [6 empty] | x
23 | 24VDC Redundancy Module | RHINO | PSM24-REM360S | 2 | Automation Direct | 159 | 318 | [6 empty] | x
24 | 15 Amp Circuit Breaker | Allen Bradley | 1492-CB1G150 | 2 | EECO | 43.99 | 87.98 | [6 empty] | x
25 | 5 Amp Circuit Breaker | Allen Bradley | 1492-CB1G050 | 18 | EECO | 46.08 | 829.44 | [6 empty] | x
26 | 2 Amp Circuit Breaker | Allen Bradley | 1489-M1C020 | 4 | EECO | 53 | 212 | [6 empty] | x
27 | Terminal block single level | Allen Bradley | 1492-J3 | 40 | EECO | 1.11 | 44.4 | [6 empty] | x
28 | Grounding Block | Allen Bradley | 1492-JG3 | 50 | EECO | 5.51 | 275.5 | [6 empty] | x
29 | End Barrier for J3 | Allen Bradley | 1492-EBJ3 | 4 | EECO | 0.83 | 3.32 | [6 empty] | x
30 | End Anchor for J3 | Allen Bradley | 1492-EAHJ35 | 25 | EECO | 4.37 | 109.25 | [6 empty] | x
31 | Terminal group marker | Allen Bradley | 1492-G35 | 26 | EECO | 3.99 | 103.74 | [6 empty] | x
35 | 10 Screw Center Jumper | Allen Bradley | 1492-CJJ5-10 | 10 | EECO | 5 | 50 | [5 empty] | price guess | x
37 | Terminal block 3 level | Allen Bradley | 1492-WTF3 | 160 | EECO | 8.39 | 1342.4 | [6 empty] | x
38 | End Barrier for WTF3 | Allen Bradley | 1492-EBTF3 | 10 | EECO | 1.74 | 17.4 | [6 empty] | x
39 | End Anchor for WTF3 | Allen Bradley | 1492-EAJ35 | 10 | EECO | 2.05 | 20.5 | [6 empty] | x
40 | 3 level + ground | Allen Bradley | 1492-JT3M | 77 | EECO | 5.4 | 415.8 | [6 empty] | x
41 | End Barrier for JT3M | Allen Bradley | 1492-EBJ3TM | 5 | EECO | 1.42 | 7.1 | [6 empty] | x
42 | Jumpers, 20 pole Red | Allen Bradley | 1492-SJT5-20-R | 10 | EECO | 9.32 | 93.2 | [6 empty] | x
43 | Jumpers, 20 pole Blue | Allen Bradley | 1492-SJT5-20-B | 10 | EECO | 9.32 | 93.2 | [6 empty] | x
44 | DIN Rail | Allen Bradley | 199-DR1 | 6 | EECO | 10.83 | 64.98 | [6 empty] | x
45 | Wire Duct | Panduit | 2X4LG6, C2X4LG6 | 120 | VAROIUS | 10 | 1200 | [6 empty] | x
49 | UPS | APC | SMX2000RMLV2U | 1 | Newegg | 1159.99 | 1159.99 | [6 empty] | x
50 | Relay Smartcard for UPS | APC | AP9613 | 1 | TigerDirect | 200 | 200 | [6 empty] | x
51 | Vertical Power Strip | Hammond | 1587T10A1 | 0 | Allied Electronics | 84.62 | 0
30 | Hookup Wire |  |  | 1500 |  | 1 | 1500 | [5 empty] | 800' @ $1/foot..
54 | Timer Relay (for watchdog) | Tyco | CNT-35-96 | 1 |  | 225 | 225 | [6 empty] | x
55 | Control Relay 3PDT | Allen Bradley | 700HA33Z24 | 1 |  | 18 | 18 | [6 empty] | x
55 | Relay for SOE (relay + base) | Finder | 44.62.7.024.4000 | 18 |  | 14 | 252 | [6 empty] | x
[5 empty] | INFRASTRUCTURE SUBTOTAL |  | 9907.2
External Cables (Between Racks & Can)
1 | Generic Cables |  |  | 30 |  | 500 | 15000 | [5 empty] | Estimated price per cable (if build by contractor)
[5 empty] | EXTERNAL CABLING SUBTOTAL |  | 15000
Heater Control Box
1 | Enclosure | Hoffman? |  | 2 |  | 100 | 200
2 | Backpanel | Hoffman? |  | 2 |  | 100 | 200
3 | Solid State Relay |  |  | 2 |  | 50 | 100
4 | Interposing Relay + Base | Finder | Same as EV's | 4 |  | 60 | 240
5 | Din Rail | Allen Bradley | 199-DR1 | 2 |  | 10.83 | 21.66
6 | Terminal block single level | Allen Bradley | 1492-J3 | 20 | EECO | 1.11 | 22.2
7 | Grounding Block | Allen Bradley | 1492-JG3 | 4 | EECO | 5.51 | 22.04
8 | End Barrier for J3 | Allen Bradley | 1492-EBJ3 | 4 | EECO | 0.83 | 3.32
9 | End Anchor for J3 | Allen Bradley | 1492-EAHJ35 | 6 | EECO | 4.37 | 26.22
10 | Terminal group marker | Allen Bradley | 1492-G35 | 4 | EECO | 3.99 | 15.96
11 | Hookup Wire |  |  | 60 |  | 1 | 60 | [5 empty] | 60' @ $1/foot…
12 | Heaters (Immersion) | Chromalox |  | 2 |  | 100 | 200
13 | Feedthrough | Kurt J Lesker |  | 2 |  | 250 | 500
14 | Vacuum Connector | Kurt J Lesker |  | 2 |  | 125 | 250
15 | Air Side Connector | Kurt J Lesker |  | 2 |  | 125 | 250
16 | LHe Reservoir Heaters | AMTEK | DLM60-10M13M51A | 2 |  | 1159.99 | 2319.98
17 | Rack Mount Hardware kit | AMTEK | DLMRK | 2 |  | 60 | 120
18 |  |  |  | 2
[5 empty] | HEATER CONTROLS SUBTOTAL |  | 4551.38
Power Supply Communications
18 | RS232 to Ethernet/IP | Real Time Automation | 435-NBX | 1 | Real Time Automation | 715 | 715 | [6 empty] | x
|  |  |  | PLC COMMUNICATIONS SUBTOTAL |  |  | 715

## TB's
| Analog Output | Analog Input (Current) | Analog Input (Voltage) | Digital Output - Relay | Digital Input - Sinking | Digital Input - Sourcing | Digital Input - SOE | 24 VDC (10 circuit)
1492-J3 | [7 empty] | 19
1492-EBJ3 | [7 empty] | 2
1492-JT3M | 10 | 19 | 19
1492-EBJT3M | 1 | 1 | 1
1492-GM35 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2
1492-WTF3 |  |  |  | 16 |  | 33 | 16
1492-EBTF3 |  |  |  | 1 |  | 1 | 1
1492-JD3 |  |  |  |  | 33
1492-EBJD3 |  |  |  |  | 1

## Solenoid PLC Channel Layout
Power Supply
2017-05-26 |  |  |  |  | HALL B SOLENOID | [6 empty] | PLC (processor)
[5 empty] | LOCAL PLC 0: I / O CHANNEL LOCATIONS | [6 empty] | Communication
NOT USED
Chassis 0: | Slot 0 | PLC Channels | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 | Slot 9 | UNDIFINED
1756-PA72 | 1756-L72 | LOCAL | 1756-OF8 | 1756-OF8 | 1756-N2 | 1756-IF16 | 1756-IF16 | 1756-IF16 | 1756-N2 | 1756-EWEB | 1756-EN2T | SLOT FILLER
|  | Bit/Channel 00 | Slot 1: PV 8600; Slot 2: FV8621A_OUT; Slot 4: PT8620 4K He LEAD RESERVOIR; Slot 5: HTR8620 VOLTAGE_IN; Slot 6: TC8600 VAC THERMOCOUPLE | REMOVED
|  | Bit/Channel 01 | Slot 2: FV8621B_OUT; Slot 4: PT8670 4K He MAGNET RESVR.; Slot 5: HTR8620 CURRENT_IN; Slot 6: LL8620SC LHe LEVEL | ADDED
|  | Bit/Channel 02 | Slot 2: HTR8620 VOLTAGE_OUT; Slot 4: PT8675A; Slot 5: HTR8672 VOLTAGE_IN; Slot 6: LL8670SC LHe LEVEL
|  | Bit/Channel 03 | Slot 2: HTR8620 CURRENT_OUT; Slot 4: PS8677 GUARD VAC. SPEED; Slot 5: HTR8672 CURRENT_IN
|  | Bit/Channel 04 | Slot 2: HTR8672 VOLTAGE_OUT; Slot 4: PT8677 GUARD INLET; Slot 6: CG8606 VACUUM
|  | Bit/Channel 05 | Slot 2: HTR8672 CURRENT_OUT; Slot 4: LL8620DP Lhe LEAD RESVR. DP; Slot 6: CG8600TB VACUUM
|  | Bit/Channel 06 | Slot 2: HALL SENSOR CURRENT_OUT; Slot 4: LL8670DP Lhe MAG. RESVR. DP; Slot 6: TB8600 TURBO SPEED
|  | Bit/Channel 07 | Slot 4: PT86XX SPARE
|  | Bit/Channel 08 | Slot 4: PT86XX SPARE
Bit/Channel 09 | bar: Slot 7 to Slot 8
|  | Bit/Channel 10 | Slot 5: FI8621A LEAD A FLOW_CONTROL
|  | Bit/Channel 11 | Slot 5: FI8621B LEAD B FLOW_CONTROL
|  | Bit/Channel 12 | Slot 5: EV8611CD _LVDT
|  | Bit/Channel 13 | Slot 5: EV8670BY _LVDT
|  | Bit/Channel 14 | Slot 5: EV8611JT _LVDT
|  | Bit/Channel 15 | Slot 5: EV8612 _LVDT
|  |  | DWG No. -0623 Rev - | DWG No. -0624 Rev - |  | DWG No. -0626 Rev - | DWG No. -0627 Rev - | DWG No. -0628 Rev -
Power Supply
2017-05-26 |  |  | Slot 3: HALL B SOLENOID | PLC (processor)
|  |  | Slot 3: SOLENOID REMOTE PLC 1: I / O CHANNEL LOCATIONS | Communication
NOT USED
Chassis 1: | PLC Channels | Slot 0 | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Slot 5 | Slot 6 | Slot 7 | Slot 8 | Slot 9 | UNDIFINED
1756-PA72 | LOCAL | 1756-OW16I | 1756-OW16I | 1756-OW16I | 1756-N2 | 1756-IB32 | 1756-IV32 | 1756-IV32 | 1756-IB16ISOE | 1756-N2 | 1756EN2T | SLOT FILLER
| Bit/Channel 00 | EV8611CD_OPEN | KEEP_ALIVE_RESET | SV8622_OPEN |  | HTR8620 _READBACK | QD1_CH1_L1 | QD3_CH1_L1 | LEAD TEMPERATURE |  |  | REMOVED
| Bit/Channel 01 | EV8611CD_CLOSE |  | SV8678CR OPEN |  | HTR8672 _READBACK | QD1_CH1_U1 | QD3_CH1_U1 | Lhe LIQUID LEVEL_8620SC |  |  | ADDED
| Bit/Channel 02 | EV8670BY_OPEN |  | SV8678DV OPEN |  | 24VDC_BAD _LOCAL | QD1_CH2_L2 | QD3_CH2_L2 | Lhe LIQUID LEVEL_8670SC
| Bit/Channel 03 | EV8670BY_CLOSE |  | SV8675BY OPEN |  | UPS_LOW | QD1_CH2_U2 | QD3_CH2_U2 | CRYOCONS RELAY 1
| Bit/Channel 04 | Slot 0: EV8611JT_OPEN; Slot 4: UPS_ON_BATT; Slot 5: QD1_CH3_L3; Slot 6: QD3_CH3_L3; Slot 7: CRYOCONS RELAY 2
| Bit/Channel 05 | Slot 0: EV8611JT_CLOSE; Slot 4: 24VDC_BAD _REMOTE; Slot 5: QD1_CH3_U3; Slot 6: QD3_CH3_U3
| Bit/Channel 06 | Slot 0: EV8612_OPEN; Slot 4: PV8600 OPEN; Slot 5: QD1_CH4_L4; Slot 6: QD3_CH4_L4; Slot 7: PLC_FAST_DUMP
| Bit/Channel 07 | Slot 0: EV8612_CLOSE; Slot 5: QD1_CH4_U4; Slot 6: QD3_CH4_U4; Slot 7: VACUUM SUM INTERLOCK
| Bit/Channel 08 | Slot 0: HTR8620 EXTERNAL-OFF; Slot 7: WATCHDOG
| Bit/Channel 09 | Slot 0: HTR8620 ENABLE_ON
| Bit/Channel 10 | Slot 0: HTR8672 EXTERNAL-OFF; Slot 1: H. S. CURRENT SOURCE POLARITY; Slot 7: VT_CABLE_ INTLCK
| Bit/Channel 11 | Slot 0: HTR8672 ENABLE_ON; Slot 1: PLC_FAST_DUMP; Slot 5: PSU_480V_ON; Slot 7: SYSTEM_CABLE _INTERLOCK
| Bit/Channel 12 | Slot 1: PLC_FAST_DUMP _BACKUP; Slot 5: PSU_MAIN _POWER; Slot 7: FAST QD1 _INTERLOCK
| Bit/Channel 13 | Slot 1: PLC_SLOW_DUMP; Slot 5: PSU_SUM _INTERLOCKS; Slot 7: FAST QD2 _INTERLOCK
| Bit/Channel 14 | Slot 0: HTR8621_A SSR1_ON; Slot 1: KEEP_ALIVE _CONTROL; Slot 5: PSU_READY; Slot 7: FAST QD3 _INTERLOCK
| Bit/Channel 15 | Slot 0: HTR8621_B SSR2_ON; Slot 1: MPS_CPU_RESET; Slot 2: PV8674 OPEN; Slot 5: DUMP_SWITCH _STATUS; Slot 7: FAST QD4 _INTERLOCK
| Bit/Channel 16 | Slot 5: QD2_CH1_L1; Slot 6: QD4_CH1_L1
| Bit/Channel 17 | Slot 5: QD2_CH1_U1; Slot 6: QD4_CH1_U1
| Bit/Channel 18 | Slot 5: QD2_CH2_L2; Slot 6: QD4_CH2_L2 |  | 0
| Bit/Channel 19 | Slot 5: QD2_CH2_U2; Slot 6: QD4_CH2_U2
| Bit/Channel 20 | Slot 5: QD2_CH3_L3; Slot 6: QD4_CH3_L3
| Bit/Channel 21 | Slot 5: QD2_CH3_U3; Slot 6: QD4_CH3_U3
| Bit/Channel 22 | Slot 5: QD2_CH4_L4; Slot 6: QD4_CH4_L4
| Bit/Channel 23 | Slot 5: QD2_CH4_U4; Slot 6: QD4_CH4_U4
Bit/Channel 24 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 25 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 26 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 27 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 28 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 29 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 30 | bar: Slot 0 to Slot 2; Slot 7
Bit/Channel 31 | bar: Slot 0 to Slot 2; Slot 7
|  | DWG No. -0638 Rev - | DWG No. -0639 Rev - | DWG No. -0640 Rev - |  | DWG No. -0641 Rev - | DWG No. -0642 Rev - | DWG No. -0643 Rev - | DWG No. -0645 Rev -

## LV Chassis Layout
2017-05-19
Solenoid Chassis Layout -- view is looking at the back of the chassis
CHASSIS 1
| TR |  |  | TP |  | SPARES |  | LC
| J1 |  | J5 | J9 | J13 | J17 | J21 | J25 |  | Spares Chassis 1
| J2 |  | J6 | J10 | J14 | J18 | J22 | J26 |  | 8
| J3 |  | J7 | J11 | J15 | J19 | J23 | J27
| J4 |  | J8 | J12 | J16 | J20 | J24 | J28
CHASSIS 2
| TR |  |  | TP |  | HS | SPARES | LC
| J1 |  | J5 | J9 | J13 | J17 | J21 | J25 |  | Spares Chassis2
| J2 |  | J6 | J10 | J14 | J18 | J22 | J26 |  | 15
| J3 |  | J7 | J11 | J15 | J19 | J23 | J27
| J4 |  | J8 | J12 | J16 | J20 | J24 | J28
Each connector has 2 channels (A, B) - cryocon pinout
LC channel can also be HS channel. Excitation is provided by external source for HS.
|  | PLC Arrays | [15 empty] | CHANGE THIS DATA TO ADJUST THE DEFAULT VALUES FOR THE SENSOR TYPES!
|  | Name | Size* | *element 0 of each array is a counter -- | [14 empty] | Excitation | AC/DC | Excitation | Calibration | PLC Units
|  | LC_From_Sol_cRIO | 16 | cRIO to increment by 1 each time the array is updated -- roll over to 0 at 2^31 | [13 empty] | TR | I | AC | .3-10 | LOOKUP | K
|  | SG_From_Sol_cRIO | 0 | [14 empty] | SG | V | DC | 5 | FORMULA | nV/V
|  | PT_From_Sol_cRIO | 15 | [14 empty] | TP | I | DC | 2.5 | LOOKUP | K
|  | TR_From_Sol_cRIO | 26 | [14 empty] | LC | V | DC | 5 | LOOKUP | lb
|  | HS_From_Sol_cRIO | 3 | [14 empty] | HS | V | DC | 2.5 | LOOKUP | G
[18 empty] | ELSE | ????? | ????? | ????? | ????? | ?????
Dwg. # | Name from Vendor | Jlab PV Name | Chassis | Connector | Channel | Type (TR, SG,…) | Serial # | Location/Description | Excitation | AC/DC | Excitation (uA or V) | Calibrated? | Read Register Address | Write Register Address | Calib. Type | PLC Tag (DINT) | PLC Tag Type | PLC Units | Notes
-0665 | TS01 | TR86101CP_B | 1 | J1 | A | TR | X100007 | Cooling Plate Lower TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 38 | 0 | LOOKUP | TR_From_Sol_cRIO[1] | DINT | K
-0665 | TS02 | TR86102CP_B | 1 | J1 | B | TR | X99799 | Cooling Plate Lower TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 39 | 1 | LOOKUP | TR_From_Sol_cRIO[2] | DINT | K
-0665 | TS03 | TR86103CP_T | 1 | J2 | A | TR | X99776 | Cooling Plate Upper TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 3a | 2 | LOOKUP | TR_From_Sol_cRIO[3] | DINT | K
-0665 | TS04 | TR86104CP_T | 1 | J2 | B | TR | X99801 | Cooling Plate Upper TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 3b | 3 | LOOKUP | TR_From_Sol_cRIO[4] | DINT | K
-0665 | TS05 | TR86105C1 | 1 | J3 | A | TR | X99453 | Coil 1 ID Upper TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 3c | 4 | LOOKUP | TR_From_Sol_cRIO[5] | DINT | K
-0665 | TS06 | TR86106C1 | 1 | J3 | B | TR | X101015 | Coil 1 ID Upper TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 3d | 5 | LOOKUP | TR_From_Sol_cRIO[6] | DINT | K
-0665 | TS07 | TR86107C2 | 1 | J4 | A | TR | X100862 | Coil 2 ID Upper TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 3e | 6 | LOOKUP | TR_From_Sol_cRIO[7] | DINT | K
-0665 | TS08 | TR86108C2 | 1 | J4 | B | TR | X99452 | Coil 2 ID Upper TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 3f | 7 | LOOKUP | TR_From_Sol_cRIO[8] | DINT | K
-0665 | TS09 | TR86109C3 | 1 | J5 | A | TR | X101013 | Coil 3 OD Upper TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 40 | 8 | LOOKUP | TR_From_Sol_cRIO[9] | DINT | K
-0666 | TS10 | TR86110C3 | 2 | J2 | A | TR | X101016 | Coil 3 OD Upper TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 3a | 2 | LOOKUP | TR_From_Sol_cRIO[10] | DINT | K
-0667 | TS11 | TR86111C4 | 2 | J3 | A | TR | X99428 | Coil 4 OD Upper TS1 | LOOKUP | AC | 0.3 - 20 | Yes | 3c | 4 | LOOKUP | TR_From_Sol_cRIO[11] | DINT | K
-0667 | TS12 | TR86112C4 | 2 | J3 | B | TR | X101014 | Coil 4 OD Upper TS2 | LOOKUP | AC | 0.3 - 20 | Yes | 3d | 5 | LOOKUP | TR_From_Sol_cRIO[12] | DINT | K
-0667 | TS13 | TR86113C5 | 2 | J4 | A | TR | X110276 | Coil 5 OD Upper TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 3e | 6 | LOOKUP | TR_From_Sol_cRIO[13] | DINT | K
-0667 | TS14 | TR86114C5 | 2 | J4 | B | TR | X110277 | Coil 5 OD Upper TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 3f | 7 | LOOKUP | TR_From_Sol_cRIO[14] | DINT | K
-0666 | TS15 | TR86115SP_C1_C3 | 1 | J6 | A | TR | X109521 | Splice 1 TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 42 | a | LOOKUP | TR_From_Sol_cRIO[15] | DINT | K
-0666 | TS16 | TR86116SP_C1_C3 | 1 | J6 | B | TR | X109519 | Splice 1 TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 43 | b | LOOKUP | TR_From_Sol_cRIO[16] | DINT | K
-0666 | TS17 | TR86117SP_C3_C5 | 1 | J7 | A | TR | X109522 | Splice 2 TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 44 | c | LOOKUP | TR_From_Sol_cRIO[17] | DINT | K
-0666 | TS18 | TR86118SP_C3_C5 | 1 | J7 | B | TR | X109494 | Splice 2 TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 45 | d | LOOKUP | TR_From_Sol_cRIO[18] | DINT | K
-0666 | TS19 | TR86119SP_C4_C5 | 1 | J8 | A | TR | X110279 | Splice 5 TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 46 | e | LOOKUP | TR_From_Sol_cRIO[19] | DINT | K
-0666 | TS20 | TR86120SP_C4_C5 | 1 | J8 | B | TR | X109520 | Splice 5 TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 47 | f | LOOKUP | TR_From_Sol_cRIO[20] | DINT | K
-0666 | TS21 | TR86121SP_C2_C4 | 2 | J1 | A | TR | X109493 | Splice 6 TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 38 | 0 | LOOKUP | TR_From_Sol_cRIO[21] | DINT | K
-0666 | TS22 | TR86122SP_C2_C4 | 2 | J1 | B | TR | X110278 | Splice 6, TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 39 | 1 | LOOKUP | TR_From_Sol_cRIO[22] | DINT | K
-0667 | TS23 | TR86123RS_US_T_BL_C | 2 | J5 | A | TR | X110290 | Suspension 5 CM TS | LOOKUP | AC | 0.3 - 20 | Yes | 40 | 8 | LOOKUP | TR_From_Sol_cRIO[23] | DINT | K
-0667 | TS24 | TR86124RS_DS_B_BL_C | 2 | J5 | B | TR | X110287 | Suspension 7 CM TS | LOOKUP | AC | 0.3 - 20 | Yes | 41 | 9 | LOOKUP | TR_From_Sol_cRIO[24] | DINT | K
-0667 | TS25 | TP86125RS_US_T_BL_M | 1 | J9 | A | TP | P31432 | Suspension 5 Midlink TS 1 | LOOKUP | DC | 2500 | Yes | 48 | 10 | LOOKUP | PT_From_Sol_cRIO[1] | DINT | K
-0667 | TS26 | TP86126RS_US_T_BL_M | 1 | J9 | B | TP | P31433 | Suspension 5 Midlink TS 2 | LOOKUP | DC | 2500 | Yes | 49 | 11 | LOOKUP | PT_From_Sol_cRIO[2] | DINT | K
-0667 | TS27 | TP86127RS_DS_B_BL_M | 1 | J10 | A | TP | P31444 | Suspension 7 Midlink TS | LOOKUP | DC | 2500 | Yes | 4a | 12 | LOOKUP | PT_From_Sol_cRIO[3] | DINT | K
-0668 | TS28 | TP86128HS_BO_B_BR | 1 | J11 | A | TP | P31491 | Rad Shield Bore Lower TS 1 | LOOKUP | DC | 2500 | Yes | 4c | 14 | LOOKUP | PT_From_Sol_cRIO[4] | DINT | K
-0668 | TS29 | TP86129HS_BO_B_BL | 1 | J11 | B | TP | P32302 | Rad Shield Bore Lower TS 2 | LOOKUP | DC | 2500 | Yes | 4d | 15 | LOOKUP | PT_From_Sol_cRIO[5] | DINT | K
-0668 | TS30 | TP86130HS_B_OD | 1 | J12 | A | TP | P32304 | Rad Shield OD Lower TS 1 | LOOKUP | DC | 2500 | Yes | 4e | 16 | LOOKUP | PT_From_Sol_cRIO[6] | DINT | K
-0668 | TS31 | TP86131HS_B_OD | 1 | J12 | B | TP | P32305 | Rad Shield OD Lower TS 2 | LOOKUP | DC | 2500 | Yes | 4f | 17 | LOOKUP | PT_From_Sol_cRIO[7] | DINT | K
-0668 | TS32 | TR86132BOB_US | 2 | J6 | A | TR | X110289 | C1-4 Bobbin TS 1 | LOOKUP | AC | 0.3 - 20 | Yes | 42 | a | LOOKUP | TR_From_Sol_cRIO[25] | DINT | K
-0668 | TS33 | TR86133BOB_DS | 2 | J6 | B | TR | X110288 | C1-4 Bobbin TS 2 | LOOKUP | AC | 0.3 - 20 | Yes | 43 | b | LOOKUP | TR_From_Sol_cRIO[26] | DINT | K
-0668 | TS34 | TP86134HS_US_CO_LBR | 1 | J13 | A | TP | P32306 | Rad Shield Cone TS 1 | LOOKUP | DC | 2500 | Yes | 50 | 18 | LOOKUP | PT_From_Sol_cRIO[8] | DINT | K
-0669 | TS35 | TP86135HS_DS_CO_XXX | 1 | J14 | A | TP | P32307 | Rad Shield Cone TS 2 | LOOKUP | DC | 2500 | Yes | 52 | 1a | LOOKUP | PT_From_Sol_cRIO[9] | DINT | K
-0669 | TS36 | TP86136HS_DS_CO_XXX | 1 | J14 | B | TP | P32308 | Rad Shield Cone TS 3 | LOOKUP | DC | 2500 | Yes | 53 | 1b | LOOKUP | PT_From_Sol_cRIO[10] | DINT | K
-0669 | TS37 | TP86137HS_US_CO_UBR | 1 | J15 | A | TP | P32310 | Rad Shield Cone TS 4 | LOOKUP | DC | 2500 | Yes | 54 | 1c | LOOKUP | PT_From_Sol_cRIO[11] | DINT | K
-0669 | TS38 | TP86138HS_US_CO_UBL | 1 | J15 | B | TP | P32311 | Rad Shield Cone TS 5 | LOOKUP | DC | 2500 | Yes | 55 | 1d | LOOKUP | PT_From_Sol_cRIO[12] | DINT | K
-0669 | TS39 | TP86139HS_DS_CO_UBL | 1 | J16 | A | TP | P32315 | Rad Shield Cone TS 6 | LOOKUP | DC | 2500 | Yes | 56 | 1e | LOOKUP | PT_From_Sol_cRIO[13] | DINT | K
-0669 | TS40 | TP86140HS_DS_CO_LBL | 1 | J16 | B | TP | P32314 | Rad Shield Cone TS 7 | LOOKUP | DC | 2500 | Yes | 57 | 1f | LOOKUP | PT_From_Sol_cRIO[14] | DINT | K
-0669 | TS41 | TP86141HS_US_CO_LBL | 2 | J9 | A | TP | P32316 | Rad Shield Cone TS 8 | LOOKUP | DC | 2500 | Yes | 48 | 10 | LOOKUP | PT_From_Sol_cRIO[15] | DINT | K
-0662-1 | RLC86701-RL07 | RS86107DS_BL_B | 1 | J25 | A | LC | 200610240 | Solenoid DS BL Radial Support Lower | LOOKUP | DC | 5 | Yes | 68 | 30 | LOOKUP | LC_From_Sol_cRIO[1] | DINT | lb
-0662-1 | ALC86701-AL07 | ZS86107DS_BL_B | 1 | J25 | B | LC | 310292 | Solenoid DS BL Axial Support Lower | LOOKUP | DC | 5 | Yes | 69 | 31 | LOOKUP | LC_From_Sol_cRIO[2] | DINT | lb
-0662-1 | RLC86704-RL06 | RS86106DS_BL_T | 1 | J26 | A | LC | 200610239 | Solenoid DS BL Radial Support Upper | LOOKUP | DC | 5 | Yes | 6a | 32 | LOOKUP | LC_From_Sol_cRIO[3] | DINT | lb
-0662-1 | ALC86704-AL06 | ZS86106DS_BL_T | 1 | J26 | B | LC | 310291 | Solenoid DS BL Axial Support Upper | LOOKUP | DC | 5 | Yes | 6b | 33 | LOOKUP | LC_From_Sol_cRIO[4] | DINT | lb
-0662-2 | RLC86705-RL03 | RS86103DS_BR_T | 1 | J27 | A | LC | 200610235 | Solenoid DS BR Radial Support Upper | LOOKUP | DC | 5 | Yes | 6c | 34 | LOOKUP | LC_From_Sol_cRIO[5] | DINT | lb
-0662-2 | ALC86705-AL03 | ZS86103DS_BR_T | 1 | J27 | B | LC | 310288 | Solenoid DS BR Axial Support Upper | LOOKUP | DC | 5 | Yes | 6d | 35 | LOOKUP | LC_From_Sol_cRIO[6] | DINT | lb
-0662-2 | RLC86708-RL02 | RS86102DS_BR_B | 1 | J28 | A | LC | 200610233 | Solenoid DS BR Radial Support Lower | LOOKUP | DC | 5 | Yes | 6e | 36 | LOOKUP | LC_From_Sol_cRIO[7] | DINT | lb
-0662-2 | ALC86708-AL02 | ZS86102DS_BR_B | 1 | J28 | B | LC | 310287 | Solenoid DS BR Axial Support Lower | LOOKUP | DC | 5 | Yes | 6f | 37 | LOOKUP | LC_From_Sol_cRIO[8] | DINT | lb
-0662-3 | RLC86703-RL05 | RS86105US_BL_T | 2 | J25 | A | LC | 200610237 | Solenoid US BL Radial Support Upper | LOOKUP | DC | 5 | Yes | 68 | 30 | LOOKUP | LC_From_Sol_cRIO[9] | DINT | lb
-0662-3 | ALC86703-AL05 | ZS86105US_BL_T | 2 | J25 | B | LC | 310290 | Solenoid US BL Axial Support Upper | LOOKUP | DC | 5 | Yes | 69 | 31 | LOOKUP | LC_From_Sol_cRIO[10] | DINT | lb
-0662-3 | RLC86702-RL08 | RS86108US_BL_B | 2 | J26 | A | LC | 201610067 | Solenoid US BL Radial Support Lower | LOOKUP | DC | 5 | Yes | 6a | 32 | LOOKUP | LC_From_Sol_cRIO[11] | DINT | lb
-0662-3 | ALC86702-AL08 | ZS86108US_BL_B | 2 | J26 | B | LC | 310293 | Solenoid US BL Axial Support Lower | LOOKUP | DC | 5 | Yes | 6b | 33 | LOOKUP | LC_From_Sol_cRIO[12] | DINT | lb
-0662-4 | RLC86706-RL04 | RS86104US_BR_T | 2 | J27 | A | LC | 200610236 | Solenoid US BR Radial Support Upper | LOOKUP | DC | 5 | Yes | 6c | 34 | LOOKUP | LC_From_Sol_cRIO[13] | DINT | lb
-0662-4 | ALC86706-AL04 | ZS86104US_BR_T | 2 | J27 | B | LC | 310289 | Solenoid US BR Axial Support Upper | LOOKUP | DC | 5 | Yes | 6d | 35 | LOOKUP | LC_From_Sol_cRIO[14] | DINT | lb
-0662-4 | RLC86707-RL01 | RS86101US_BR_B | 2 | J28 | A | LC | 200610232 | Solenoid US BR Radial Support Lower | LOOKUP | DC | 5 | Yes | 6e | 36 | LOOKUP | LC_From_Sol_cRIO[15] | DINT | lb
-0662-4 | ALC86707-AL01 | ZS86101US_BR_B | 2 | J28 | B | LC | 310277 | Solenoid US BR Axial Support Lower | LOOKUP | DC | 5 | Yes | 6f | 37 | LOOKUP | LC_From_Sol_cRIO[16] | DINT | lb
-0662-5 | HS1 | HS1 | 2 | J17 | A | HS |  | Solenoid DS end (0 deg) | LOOKUP | DC | 2.5 | No | 56 | 1e | LOOKUP | HS_From_Sol_cRIO[1] | DINT | G
-0662-5 | HS2 | HS2 | 2 | J18 | A | HS |  | Solenoid DS end (120 deg) | LOOKUP | DC | 2.5 | No | 58 | 20 | LOOKUP | HS_From_Sol_cRIO[2] | DINT | G
-0662-6 | HS3 | HS3 | 2 | J18 | B | HS |  | Solenoid DS end (240 deg) | LOOKUP | DC | 2.5 | No | 59 | 21 | LOOKUP | HS_From_Sol_cRIO[3] | DINT | G
Note on V24: Renuka Rajput-Ghoshal: The excitation current for cernox sensors is constant current with current "varied for different temperature range (based on resistance and power)". The resistance measurement is based on differential values of excitation current and read out voltage at temperatures.

## CRYOCON MAPS
2017-05-19
SOLENOID
CRYOCON MAPPING
CRYOCON 1 |  |  |  | CRYOCON 2 |  |  |  | CRYOCON 3
Channel | PV | Serial No. | PLC channel | Channel | PV | Serial No. | PLC channel | Channel | PV | Serial No. | PLC channel
A | TR8622A | X100355 | CryoCon1.Temperatures[0] | A | TR8670 | X103728 | CryoCon2.Temperatures[0] | A | TP8622A | WCL1 | CryoCon3.Temperatures[0]
redundant | TR8622Ar | X100312 |  | redundant | TR8670r | X103236 |  |  |  | 215
B | TR8622B | X103646 | CryoCon1.Temperatures[1] | B | TR8673 | X103692 | CryoCon2.Temperatures[1] | B | TP8622Ar | WCL1 | CryoCon3.Temperatures[1]
redundant | TR8622Br | X100394 |  | redundant | TR8673r | X103693 |  |  |  | 216
C | TR8611 | X103241 | CryoCon1.Temperatures[2] | C | TR8674 | X103739 | CryoCon2.Temperatures[2] | C | TP8622B | WCL2 | CryoCon3.Temperatures[2]
redundant | TR8611r | X103326 |  | redundant | TR8674r | X103713 |  |  |  | 241
D | TR8672 | X103328 | CryoCon1.Temperatures[3] | D | TP8680 | 211 | CryoCon2.Temperatures[3] | D | TP8622Br | WCL2 | CryoCon3.Temperatures[3]
redundant | TR8672r | X103689 |  | redundant | TP8680r | 212 |  |  |  | 242
E | TR8671 | X103690 | CryoCon1.Temperatures[4] | E | TR8624A | X103735 | CryoCon2.Temperatures[4] | E | TP8611 | 205 | CryoCon3.Temperatures[4]
redundant | TR8671r | X103691 |  | SPARE |  |  |  | redundant | TP8611r | 206
F |  |  | CryoCon1.Temperatures[5] | F | TR8624B | X103736 | CryoCon2.Temperatures[5] | F | TP8620A | 213 | CryoCon3.Temperatures[5]
redundant |  |  |  | SPARE |  |  |  | redundant | TP8620Ar | 214
G | TR8610 | X111832 | CryoCon1.Temperatures[6] | G | TP8621A | 179 | CryoCon2.Temperatures[6] | G | TP8620B | 223 | CryoCon3.Temperatures[6]
|  |  |  | redundant | TP8621Ar | 180 |  | redundant | TP8620Br | 224
H | TR8610r | X111864 | CryoCon1.Temperatures[7] | H | TP8621B | 227 | CryoCon2.Temperatures[7] | H | TP8675 | 169 | CryoCon3.Temperatures[7]
|  |  |  | redundant | TP8621Br | 228 |  | redundant | TP8675r | 170

## Solenoid BOM
No. | Item | Mfg | PN | Qty | Vendor | Quote Unit Price | Total Est. Price | Date Ordered | Date Expected | PR# | Total Acutal Price | Location | NOTES:
1 | Rack | - | - | 1 | ? | 0 | 0 | N/A |  | N/A |  | Hall B | Already on hand
2 | Back Panel |  |  | 3 |  | 300 | 900 | [5 empty] | Guess
3 | 10-Slot Chassis | Allen Bradley | 1756-A10 | 2 | EECO | 478.04 | 956.08
4 | Power Supply | Allen Bradley | 1756-PA72 | 2 | EECO | 708.18 | 1416.36
5 | PLC | Allen Bradley | 1756-L72 | 1 | EECO | 5964.4 | 5964.4
6 | Ethernet Module | Allen Bradley | 1756-EN2T | 2 | EECO | 2123.8 | 4247.6
7 | Ethernet Gateway | Allen Bradley | 1756-EWEB | 1 | EECO | 2331 | 2331 | [5 empty] | May not be necessary
8 | Digital Relay Output Module (16 ch) | Allen Bradley | 1756-OW16I | 3 | EECO | 485.44 | 1456.32
9 | RTB Jumper for OW16I | Allen Bradley | 1756-JMPR | 3 | EECO | 5 | 15 | [5 empty] | Estimated Price
10 | Analog Input Module (16 ch) | Allen Bradley | 1756-IF16 | 1 | EECO | 1206.2 | 1206.2
11 | Digital Input Module, 24 VDC Sink | Allen Bradley | 1756-IB32 | 1 | EECO | 396.26 | 396.26 | [5 empty] | Estimated Price
12 | Sequence of Events Module | Allen Bradley | 1756-IB16ISOE | 1 | EECO | 664.52 | 664.52
13 | Analog Output Module (8 ch) | Allen Bradley | 1756-OF8 | 3 | EECO | 1554 | 4662
14 | Module Terminal Block (16 ch) | Allen Bradley | 1756-TBCH | 9 | EECO | 65.12 | 586.08
15 | Module Terminal Block (8 ch) | Allen Bradley | 1756-TBNH | 3 | EECO | 52.54 | 157.62
16 | Slot Filler | Allen Bradley | 1756-N2 | 6 | EECO | 25 | 150 | [5 empty] | Estimated Price
17 | TCP to Ethernet/IP | Real Time Automation | 490-NBX | 1 | Real Time Automation | 715 | 715 | [5 empty] | Could also be 460ETCTCP (does parsing), same price
18 | RS232 to Ethernet/IP | Real Time Automation | 435-NBX | 1 | Real Time Automation | 715 | 715
19 | LVDT Excitation/Readback | Macro Sensors | LVC-2500 | 4 | Macro Sensors | 521 | 2084
20 | CryoCon Temperature Monitor (8 ch) | CryoCon | 18C | 3 | CryoCon | 1695 | 5085
21 | CryoCon Panel Mount Kit | CryoCon | 3014-020 | 3 | CryoCon | 30 | 90
22 | 24 VDC Power Supply | RHINO | PSM24-360S | 4 | Automation Direct | 229 | 916
23 | 24VDC Redundancy Module | RHINO | PSM24-REM360S | 2 | Automation Direct | 159 | 318
24 | 15 Amp Circuit Breaker | Allen Bradley | 1492-CB1G150 | 2 | EECO | 43.99 | 87.98
25 | 5 Amp Circuit Breaker | Allen Bradley | 1492-CB1G050 | 18 | EECO | 46.08 | 829.44
26 | 2 Amp Circuit Breaker | Allen Bradley | 1489-M1C020 | 4 | EECO | 46.08 | 184.32
27 | Terminal block single level | Allen Bradley | 1492-J3 | 20 | EECO | 0.75 | 15
28 | Grounding Block | Allen Bradley | 1492-JG3 | 50 | EECO | 5.51 | 275.5
29 | End Barrier for J3 | Allen Bradley | 1492-EBJ3-Y | 20 | EECO | 0.76 | 15.2
30 | End Anchor for J3 | Allen Bradley | 1492-EAHJ35 | 12 | EECO | 4.37 | 52.44
31 | Terminal group marker | Allen Bradley | 1492-GM35 | 10 | EECO | 3.99 | 39.9
32 | Terminal block 2 level | Allen Bradley | 1492-JDG3 | 50 | EECO | 5.82 | 291
33 | Terminal block 2 level | Allen Bradley | 1492-JD3-RE | 50 | EECO | 8.39 | 419.5
34 | Terminal block 2 level | Allen Bradley | 1492-JD3-BL | 50 | EECO | 8.39 | 419.5
35 | Terminal block 2 level | Allen Bradley | 1492-JD3-W | 50 | EECO | 8.39 | 419.5
36 | Terminal block 2 level | Allen Bradley | 1492-JD3-Y | 50 | ON-HAND | 3.62 | 181
37 | End Barrier for JD3 | Allen Bradley | 1492-EBJD3 | 20 | EECO | 0.83 | 16.6
38 | End Barrier for JD3 | Allen Bradley | 1492-EBJ3 | 2 | EECO | 0.83 | 1.66
39 | End anchor for JD3 | Allen Bradley | 1492-EAHJ35 | 29 | EECO | 4.37 | 126.73
40 | 10 Screw Center Jumper | Allen Bradley | 1492-CJJ5-10 | 10 | EECO | 5 | 50 | [5 empty] | price guess
41 | End Barrier for JG3 | Allen Bradley | 1492-EBJ3-Y | 50 | EECO | 2.3 | 115
42 | Terminal block 3 level | Allen Bradley | 1492-WTF3 | 168 | EECO | 8.39 | 1409.52
43 | End Barrier for WTF3 | Allen Bradley | 1492-EBTF3 | 12 | EECO | 1.74 | 20.88
44 | End Anchor for WTF3 | Allen Bradley | 1492-EAHJ35 | 23 | EECO | 4.37 | 100.51
45 | 3 level + ground | Allen Bradley | 1492-JT3M | 77 | EECO | 5.4 | 415.8
46 | End Barrier for JT3M | Allen Bradley | 1492-EBJ3TM | 5 | EECO | 1.42 | 7.1
47 | Jumpers, 20 pole Red | Allen Bradley | 1492-SJT5-20-R | 10 | EECO | 9.32 | 93.2
48 | Jumpers, 20 pole Blue | Allen Bradley | 1492-SJT5-20-B | 10 | EECO | 9.32 | 93.2
49 | DIN Rail | Allen Bradley | 199-DR1 | 9 | EECO | 10.83 | 97.47
50 | Wire Duct | Panduit | 2X4LG6 | 120 | BEST PRICE | 10 | 1200
51 | 10" Touch Panel (Local Control Panel for EVs) | Automation Direct | EA9-T10CL | 1 | Automation Direct | 1290 | 1290
52 | Touch Panel Software | Automation Direct | EA9-PGMSW | 0 | Automation Direct | 99 | 0
53 | Ethernet Switch | Cisco | ?? | 1 | ?? | 5000 | 5000 | [5 empty] | Guess, based on Hall D's switch purchase
54 | UPS | APC | SMX2000RMLV2U | 1 | Newegg | 1159.99 | 1159.99
55 | Relay Smartcard for UPS | APC | AP9613 | 1 | TigerDirect | 200 | 200
56 | Vertical Power Strip | Hammond | 1587T10A1 | 2 | Allied Electronics | 84.62 | 169.24
57 | AMI Liquid Level Monitor | AMI | 135 | 2 | AMI | 835 | 1670
58 | AMI Liquid Level Probe | AMI | 135 | 2 | AMI | 1500 | 3000
59 | Timer Relay (for watchdog) | Tyco | CNT-35-96 | 1 |  | 225 | 225
60 | Relay for SOE (relay + base) | Finder | 44.62.7.024.4000 | 26 |  | 30 | 780
61 | Relay for EV's (relay + base + diode module) | Finder | 95.75 SMA | 26 |  | 30 | 780
TOTALS | [6 empty] | 56284.62 | (rack hardware)
[7 empty] | 0 | (cables, $500/cable)
[6 empty] | Total | 56284.62
What's missing?
Spares
|  |  | Hookup wire….maybe $1000 |  |  | Panel wiring
[5 empty] | Includes guess on missing stuff |  | 58284.62
???Other Stuff???
Fast DAQ Prices
Signal Conditioning
Fast DAQ itself
software?
Wiring?
Voltage tap wires?
Temp/Strain Cables?
Current Limiting Resistor Box?
Voltage tap distribution box?

## Solenoid Magnet Wire Map
| Distribution Box Instruments - Sensor Connector Wire Map CM-8501A | [5 empty] | Silicone Diode | Temperatures
Distribution Box Instruments - Vacuum Port 8501A
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Silicone Diodes |  | SPLICE | Connector # 8501A5 | Connector # 8501A4 | Connector # 8501A3 |  | Connector # 8501A2 | Connector # 8501A1 | Cable
|  | TRANSITION | FTACIR32V | IFDRG327013 | FTACIR32AC |  | MS3476L20-41PY | MS3470L20-41SY | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
TR8674 | I + | CLR / YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK / BLK | B | B | B | 2 | B | B | BLU
| V- | GRN/ GRN | C | C | C | 3 | C | C | BLK
| I- | RED / RED | D | D | D | 4 | D | D | BLK
TD8512r | I + | CLR / YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK / BLK | F | F | F | 6 | F | F | BLK
| V- | GRN/ GRN | G | G | G | 7 | G | G | GRN
| I- | RED / RED | H | H | H | 8 | H | H | RED
TD8513S | I + | CLR / YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK / BLK | K | K | K | 10 | K | K | BLU
| V- | GRN/ GRN | L | L | L | 11 | L | L | BLK
| I- | RED / RED | M | M | M | 12 | M | M | BLK
TD8513Sr | I + | CLR / YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK / BLK | P | P | P | 14 | P | P | BLK
| V- | GRN/ GRN | R | R | R | 15 | R | R | GRN
| I- | RED / RED | S | S | S | 16 | S | S | RED
TD8513T | I + | CLR / YEL | T | T | T | 17 | T | T | WHT
| V+ | BLK / BLK | U | U | U | 18 | U | U | BLU
| V- | GRN/ GRN | V | V | V | 19 | V | V | BLK
| I- | RED / RED | W | W | W | 20 | W | W | BLK
TD8513r | I + | CLR / YEL | X | X | X | 21 | X | X | BLK
| V+ | BLK / BLK | Y | Y | Y | 22 | Y | Y | BLK
| V- | GRN/ GRN | Z | Z | Z | 23 | Z | Z | GRN
| I- | RED / RED | a | a | a | 24 | a | a | RED
|  |  | b | b | b | 25 | b | b
|  |  | c | c | c | 26 | c | c
|  |  | d | d | d | 27 | d | d
|  |  | e | e | e | 28 | e | e
|  |  | f | f | f | 29 | f | f
|  |  | g | g | g | 30 | g | g
Cable interlock | 24 VDC | ORG | <h> | <h> | <h> | 31 | <h> | <h> | RED
Cable interlock | 24 VDC | ORG | <j> | <j> | <j> | 32 | <j> | <j> | BLK
| Distribution Box - Sensor Connector Wire Map CM-8501B | [5 empty] | Silicon Diode | Temperatures
Distribution Box Instruments - Vacuum Port 8501B
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Silicon Diodes |  | SPLICE | Connector # 8501B5 | Connector # 8501B4 | Connector # 8501B3 |  | Connector # 8501B2 | Connector # 8501B1 | Cable
|  | TRANSITION | FTACIR32V | IFDRG327013 | FTACIR32AC | > | MS3476L18-32PX | MS3470L18-32SX | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
#REF! | I + | CLR / YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK / BLK | B | B | B | 2 | B | B | BLU
| V- | GRN/ GRN | C | C | C | 3 | C | C | BLK
| I- | RED / RED | D | D | D | 4 | D | D | BLK
#REF! | I + | CLR / YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK / BLK | F | F | F | 6 | F | F | BLK
| V- | GRN/ GRN | G | G | G | 7 | G | G | GRN
| I- | RED / RED | H | H | H | 8 | H | H | RED
#REF! | I + | CLR / YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK / BLK | K | K | K | 10 | K | K | BLU
| V- | GRN/ GRN | L | L | L | 11 | L | L | BLK
| I- | RED / RED | M | M | M | 12 | M | M | BLK
#REF! | I + | CLR / YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK / BLK | P | P | P | 14 | P | P | BLK
| V- | GRN/ GRN | R | R | R | 15 | R | R | GRN
| I- | RED / RED | S | S | S | 16 | S | S | RED
#REF! | I + | CLR / YEL | T | T | T | 17 | T | T | WHT
| V+ | BLK / BLK | U | U | U | 18 | U | U | BLU
| V- | GRN/ GRN | V | V | V | 19 | V | V | BLK
| I- | RED / RED | W | W | W | 20 | W | W | BLK
#REF! | I + | CLR / YEL | X | X | X | 21 | X | X | BLK
| V+ | BLK / BLK | Y | Y | Y | 22 | Y | Y | BLK
| V- | GRN/ GRN | Z | Z | Z | 23 | Z | Z | GRN
| I- | RED / RED | a | a | a | 24 | a | a | RED
|  |  | b | b | b | 25 | b | b
|  |  | c | c | c | 26 | c | c
|  |  | d | d | d | 27 | d | d
|  |  | e | e | e | 28 | e | e
|  |  | f | f | f | 29 | f | f
|  |  | g | g | g | 30 | g | g
Cable interlock | 24 VDC | ORG | <h> | <h> | <h> | 31 | <h> | <h> | RED
Cable interlock | 24 VDC | ORG | <j> | <j> | <j> | 32 | <j> | <j> | BLK
| Distribution Box - Sensor Connector Wire Map CM-8502A | [5 empty] | Platinum Resistors | Temperatures
Distribution Box Instruments - Vacuum Port 8502A
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Platinum Resistors |  | SPLICE | Connector # 8502A5 | Connector # 8502A4 | Connector # 8502A3 |  | Connector # 8502A2 | Connector # 8502A1 | Cable
|  | TRANSITION | FTACIR32V | IFDRG327013 | FTACIR32AC | > | MS3476L18-32PX | MS3470L18-32SX | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
TP8621B | I + | YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK | B | B | B | 2 | B | B | BLU
| V- | GRN | C | C | C | 3 | C | C | BLK
| I- | RED | D | D | D | 4 | D | D | BLK
TP8621Br | I + | YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK | F | F | F | 6 | F | F | BLK
| V- | GRN | G | G | G | 7 | G | G | GRN
| I- | RED | H | H | H | 8 | H | H | RED
#REF! | I + | YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK | K | K | K | 10 | K | K | BLU
| V- | GRN | L | L | L | 11 | L | L | BLK
| I- | RED | M | M | M | 12 | M | M | BLK
#REF! | I + | YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK | P | P | P | 14 | P | P | BLK
| V- | GRN | R | R | R | 15 | R | R | GRN
| I- | RED | S | S | S | 16 | S | S | RED
TP8676A | I + | YEL | T | T | T | 17 | T | T | WHT
| V+ | BLK | U | U | U | 18 | U | U | BLU
| V- | GRN | V | V | V | 19 | V | V | BLK
| I- | RED | W | W | W | 20 | W | W | BLK
TP8676Ar | I + | YEL | X | X | X | 21 | X | X | BLK
| V+ | BLK | Y | Y | Y | 22 | Y | Y | BLK
| V- | GRN | Z | Z | Z | 23 | Z | Z | GRN
| I- | RED | a | a | a | 24 | a | a | RED
|  |  | b | b | b | 25 | b | b
|  |  | c | c | c | 26 | c | c
|  |  | d | d | d | 27 | d | d
|  |  | e | e | e | 28 | e | e
|  |  | f | f | f | 29 | f | f
|  |  | g | g | g | 30 | g | g
Cable interlock | 24 VDC | ORG | <h> | <h> | <h> | 31 | <h> | <h> | RED
Cable interlock | 24 VDC | ORG | <j> | <j> | <j> | 32 | <j> | <j> | BLK
| Distribution Box - Sensor Connector Wire Map CM-8502B | [5 empty] | Platinum Resistors | Temperatures
Distribution Box Instruments - Vacuum Port 8502B
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Platinum Resistors |  | SPLICE | Connector # 8502B5 | Connector # 8502B4 | Connector # 8502B3 |  | Connector # 8502B2 | Connector # 8502B1 | Cable
|  | TRANSITION | FTACIR32V | IFDRG327013 | FTACIR32AC | > | MS3476L18-32PX | MS3470L18-32SX | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
0 | I + | YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK | B | B | B | 2 | B | B | BLU
| V- | GRN | C | C | C | 3 | C | C | BLK
| I- | RED | D | D | D | 4 | D | D | BLK
0r | I + | YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK | F | F | F | 6 | F | F | BLK
| V- | GRN | G | G | G | 7 | G | G | GRN
| I- | RED | H | H | H | 8 | H | H | RED
#REF! | I + | YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK | K | K | K | 10 | K | K | BLU
| V- | GRN | L | L | L | 11 | L | L | BLK
| I- | RED | M | M | M | 12 | M | M | BLK
#REF! | I + | YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK | P | P | P | 14 | P | P | BLK
| V- | GRN | R | R | R | 15 | R | R | GRN
| I- | RED | S | S | S | 16 | S | S | RED
#REF! | I + | YEL | T | T | T | 17 | T | T | WHT
| V+ | BLK | U | U | U | 18 | U | U | BLU
| V- | GRN | V | V | V | 19 | V | V | BLK
| I- | RED | W | W | W | 20 | W | W | BLK
#REF! | I + | YEL | X | X | X | 21 | X | X | BLK
| V+ | BLK | Y | Y | Y | 22 | Y | Y | BLK
| V- | GRN | Z | Z | Z | 23 | Z | Z | GRN
| I- | RED | a | a | a | 24 | a | a | RED
|  |  | b | b | b | 25 | b | b
|  |  | c | c | c | 26 | c | c
|  |  | d | d | d | 27 | d | d
|  |  | e | e | e | 28 | e | e
|  |  | f | f | f | 29 | f | f
|  |  | g | g | g | 30 | g | g
Cable interlock | 24 VDC | ORG | <h> | <h> | <h> | 31 | <h> | <h> | RED
Cable interlock | 24 VDC | ORG | <j> | <j> | <j> | 32 | <j> | <j> | BLK
| Distribution Box - Sensor Connector Wire Map CM-8503A | [5 empty] | Platinum Resistors | Temperatures
Distribution Box Instruments - Vacuum Port 8503A
THESE WIRES TO BE THERMALLY STATIONED PER 75910-0014
|  |  | Distribution Box | Distribution Box | Distribution Box |  | Controls | Controls
Temperatures |  |  | Vacuum | Feedthrough | Air |  | Cable End | Chassis mount | Control
Platinum Resistors |  | SPLICE | Connector # 8503A5 | Connector # 8503A4 | Connector # 8503A3 |  | Connector # 8503A2 | Connector # 8503A1 | Cable
|  | TRANSITION | FTACIR19V | IFDRG197013 | FTACIR19AC | > | MS3476L18-32PX | MS3470L18-32SX | Wiring
Sensor | SIGNAL | Color | SOCKET | PIN | SOCKET | P# | PIN | SOCKET | Color
#REF! | I + | YEL | A | A | A | 1 | A | A | WHT
| V+ | BLK | B | B | B | 2 | B | B | BLU
| V- | GRN | C | C | C | 3 | C | C | BLK
| I- | RED | D | D | D | 4 | D | D | BLK
#REF! | I + | YEL | E | E | E | 5 | E | E | BLK
| V+ | BLK | F | F | F | 6 | F | F | BLK
| V- | GRN | G | G | G | 7 | G | G | GRN
| I- | RED | H | H | H | 8 | H | H | RED
#REF! | I + | YEL | J | J | J | 9 | J | J | WHT
| V+ | BLK | K | K | K | 10 | K | K | BLU
| V- | GRN | L | L | L | 11 | L | L | BLK
| I- | RED | M | M | M | 12 | M | M | BLK
#REF! | I + | YEL | N | N | N | 13 | N | N | BLK
| V+ | BLK | P | P | P | 14 | P | P | BLK
| V- | GRN | R | R | R | 15 | R | R | GRN
| I- | RED | S | S | S | 16 | S | S | RED
|  |  | T | T | T | 17 | T | T
Cable interlock | 24 VDC | ORG | <U> | <U> | <U> | 18 | <U> | <U> | RED
Cable interlock | 24 VDC | ORG | <V> | <V> | <V> | 19 | <V> | <V> | BLK
OBSOLETE!

## LabView Chassis1Config File
Chassis | Tye (TR, SG,…) | Read Register Address | Write Register Address | LC Tag (DINT) | Ecitation (uA or V) | Serial #
1 | LC | 68 | 30 | LC_From_cRIO[1] | 2.5 | 200610240
1 | LC | 69 | 31 | LC_From_cRIO[2] | 2.5 | 310292
1 | LC | 6a | 32 | LC_From_cRIO[3] | 2.5 | 200610239
1 | LC | 6b | 33 | LC_From_cRIO[4] | 2.5 | 310291
1 | LC | 6c | 34 | LC_From_cRIO[5] | 2.5 | 200610235
1 | LC | 6d | 35 | LC_From_cRIO[6] | 2.5 | 310288
1 | LC | 6e | 36 | LC_From_cRIO[7] | 2.5 | 200610233
1 | LC | 6f | 37 | LC_From_cRIO[8] | 2.5 | 310287
1 | PT | 48 | 10 | T_From_CRIO[1] | 2.5 | 31432
1 | PT | 49 | 11 | T_From_CRIO[2] | 2.5 | 31433
1 | PT | 4a | 12 | T_From_CRIO[3] | 2.5 | 31444
1 | PT | 4b | 13 | T_From_CRIO[4] | 2.5 | 31491
1 | PT | 4c | 14 | T_From_CRIO[5] | 2.5 | 32302
1 | PT | 4d | 15 | T_From_CRIO[6] | 2.5 | 32304
1 | PT | 4e | 16 | T_From_CRIO[7] | 2.5 | 32305
1 | PT | 4f | 17 | T_From_CRIO[8] | 2.5 | 32306
1 | PT | 50 | 18 | T_From_CRIO[9] | 2.5 | 32307
1 | PT | 51 | 19 | T_From_CRIO[10] | 2.5 | 32308
1 | PT | 52 | 1a | T_From_CRIO[11] | 2.5 | 32310
1 | PT | 53 | 1b | T_From_CRIO[12] | 2.5 | 32311
1 | PT | 54 | 1c | T_From_CRIO[13] | 2.5 | 32315
1 | PT | 55 | 1d | T_From_CRIO[14] | 2.5 | 32314
1 | TR | 38 | 0 | TR_From_cRIO[1] | 2.5 | 100007
1 | TR | 39 | 1 | TR_From_cRIO[2] | 2.5 | 99799
1 | TR | 3a | 2 | TR_From_cRIO[3] | 2.5 | 99776
1 | TR | 3b | 3 | TR_From_cRIO[4] | 2.5 | 99801
1 | TR | 3c | 4 | TR_From_cRIO[5] | 2.5 | 99453
1 | TR | 3d | 5 | TR_From_cRIO[6] | 2.5 | 101015
1 | TR | 3e | 6 | TR_From_cRIO[7] | 2.5 | 100862
1 | TR | 3f | 7 | TR_From_cRIO[8] | 2.5 | 99452
1 | TR | 40 | 8 | TR_From_cRIO[9] | 2.5 | 101013
1 | TR | 42 | a | TR_From_cRIO[10] | 2.5 | 101016
1 | TR | 43 | b | TR_From_cRIO[11] | 2.5 | 99428
1 | TR | 44 | c | TR_From_cRIO[12] | 2.5 | 101014
1 | TR | 45 | d | TR_From_cRIO[13] | 2.5 | 110276
1 | TR | 46 | e | TR_From_cRIO[14] | 2.5 | 110277
1 | TR | 47 | f | TR_From_cRIO[15] | 2.5 | 109521

## LabView Chasis2 Config File
Chassis | Tye (TR, SG,…) | Read Register Address | Write Register Address | LC Tag (DINT) | Ecitation (uA or V) | Serial #
2 | LC | 68 | 30 | LC_From_cRIO[9] | 2.5 | 200610237
2 | LC | 69 | 31 | LC_From_cRIO[10] | 2.5 | 310290
2 | LC | 6a | 32 | LC_From_cRIO[11] | 2.5 | 201610067
2 | LC | 6b | 33 | LC_From_cRIO[12] | 2.5 | 310293
2 | LC | 6c | 34 | LC_From_cRIO[13] | 2.5 | 200610236
2 | LC | 6d | 35 | LC_From_cRIO[14] | 2.5 | 310289
2 | LC | 6e | 36 | LC_From_cRIO[15] | 2.5 | 200610232
2 | LC | 6f | 37 | LC_From_cRIO[16] | 2.5 | 310277
2 | PT | 48 | 10 | T_From_CRIO[15] | 2.5 | 32316
2 | TR | 38 | 0 | TR_From_cRIO[16] | 2.5 | 109519
2 | TR | 39 | 1 | TR_From_cRIO[17] | 2.5 | 109522
2 | TR | 3a | 2 | TR_From_cRIO[18] | 2.5 | 109494
2 | TR | 3c | 4 | TR_From_cRIO[19] | 2.5 | 110279
2 | TR | 3d | 5 | TR_From_cRIO[20] | 2.5 | 109520
2 | TR | 3e | 6 | TR_From_cRIO[21] | 2.5 | 109493
2 | TR | 3f | 7 | TR_From_cRIO[22] | 2.5 | 110278
2 | TR | 40 | 8 | TR_From_cRIO[23] | 2.5 | 110290
2 | TR | 41 | 9 | TR_From_cRIO[24] | 2.5 | 110287
2 | TR | 42 | a | TR_From_cRIO[25] | 2.5 | 110289
2 | TR | 43 | b | TR_From_cRIO[26] | 2.5 | 110288
2 | HS |  |  | HS-From_CRIO[17] | 2.5