## Sheet1
N2 Flow 1
Note limit for N2 Flow 1 Low interlock.
Note current flow setting for N2 Flow 1.
Reduce N2 Flow 1 flow using manual rotameter until interlock trips.
Verify interlock trips and HV/LV is disabled
Return N2 Flow 1 to previous setting using rotameter.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Note limit for N2 Flow 1 High Interlock
Change N2 Flow 1 High Interlock Limit to value below flow value.
Verify interlock trips and HV/LV is disabled
Return N2 Flow 1 High interlock Limit to previous setting.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
N2 Flow 2
Note limit for N2 Flow 2 Low interlock.
Note current flow setting for N2 Flow 2.
Reduce N2 Flow 2 flow using manual rotameter until interlock trips.
Verify interlock trips and HV/LV is disabled
Return N2 Flow 2 to previous setting using rotameter.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Note limit for N2 Flow 2 High Interlock
Change N2 Flow 2 High Interlock Limit to value below flow value.
Verify interlock trips and HV/LV is disabled
Return N2 Flow 2 High interlock Limit to previous setting.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Airflow 1
Note limit for Airflow 1 Low Interlock.
Note current flow setting for Airflow 1.
Reduce Airflow 1 flow using manual rotameter until interlock trips.
Verify interlock trips and HV/LV is disabled
Return Airflow 1 to previous setting.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Note limit for Airflow 1 High Interlock
Change Airflow 1 High Interlock Limit to value below flow value.
Verify interlock trips and HV/LV is disabled
Return Airflow 1 High interlock Limit to previous setting.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Airflow 2
Note limit for Airflow 2 Low Interlock.
Note current flow setting for Airflow 2.
Reduce Airflow 2 flow using manual rotameter until interlock trips.
Verify interlock trips and HV/LV is disabled
Return Airflow 2 to previous setting.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Note limit for Airflow 2 High Interlock
Change Airflow 2 High Interlock Limit to value below flow value.
Verify interlock trips and HV/LV is disabled
Return Airflow 2 High interlock Limit to previous setting.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Pressure 1
Note limit for Air Tank Pressure Low interlock.
Verify air is flowing out of tank to RICH
Turn off compressor.
Verify interlock trips and HV/LV is disabled when pressure drops below interlock limit.
Power on compressor
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Note limit for Air Tank Pressure High interlock.
Change Air Tank Pressure High interlock limit to value below current pressure reading.
Verify interlock trips and HV/LV is disabled when pressure drops below interlock limit.
Verify interlock clears
Reset latched interlocks
Verify HV/LV can be re-enabled.
Temperature
Note limit for N2 Temperature 1 Low Limit
Note current reading for N2 Temperature 1
Change N2 Temperaure 1 Low limit to a value above value noted in step above.
Verify interlock trips and HV/LV is disabled.
Return N2 Temperature 1 Low limit it its original value
Verify interlock clears for N2 Temperaure 1 Low
Reset latched interlock
Note limit for N2 Temperature 1 High Limit
Change N2 Temperaure 1 High limit to a value below value noted in step above.
Verify interlock trips and HV/LV is disabled.
Return N2 Temperature 1 High limit it its original value
Verify interlock clears for N2 Temperaure 1 High
Reset latched interlock
Repeat Test for all sensors below:
N2 Temperature 2
N2 Temperature 3
N2 Temperature 4
N2 Temperature 5
N2 Temperature 6
N2 Temperature 7
N2 Temperature 8
N2 Temperature 9
N2 Temperature 10
N2 Temperature 11
N2 Temperature 12
N2 Temperature 13
N2 Temperature 14
N2 Temperature 15
N2 Temperature 16
EP Temperature 1
EP Temperature 2
EP Temperature 3
EP Temperature 4
EP Temperature 5
EP Temperature 6
EP Temperature 7
EP Temperature 8
EP Temperature 9
EP Temperature 10
EP Temperature 11
EP Temperature 12
EP Temperature 13
EP Temperature 14
EP Temperature 15
EP Temperature 16
Humidity
Note limit for N2 Humidity 1 Low Limit
Note current reading for N2 humidity 1
Change N2 Humidity 1 Low limit to a value above value noted in step above.
Verify interlock trips and HV/LV is disabled.
Return N2 humidity 1 Low limit it its original value
Verify interlock clears for N2 humidity 1 Low
Reset latched interlock
Note limit for N2 humidity 1 High Limit
Change N2 humidity 1 High limit to a value below value noted in step above.
Verify interlock trips and HV/LV is disabled.
Return N2 humidity 1 High limit it its original value
Verify interlock clears for N2 humidity 1 High
Reset latched interlock
Repeat Test for all sensors below:
N2 Humidity 2
N2 Humidity 3
N2 Humidity 4
N2 Humidity 5
N2 Humidity 6
N2 Humidity 7
N2 Humidity 8
N2 Humidity 9
N2 Humidity 10
N2 Humidity 11
N2 Humidity 12
N2 Humidity 13
N2 Humidity 14
N2 Humidity 15
N2 Humidity 16
EP Humidity 1
EP Humidity 2
EP Humidity 3
EP Humidity 4
EP Humidity 5
EP Humidity 6
EP Humidity 7
EP Humidity 8
EP Humidity 9
EP Humidity 10
EP Humidity 11
EP Humidity 12
EP Humidity 13
EP Humidity 14
EP Humidity 15
EP Humidity 16