## HMS Quads
Quad's PLC I/O Usage Table
Module | IV16 | IB16D | OW16I | OW16I | IF16 | IF16 | IF16 | OF6VI | IF16
Configuration |  |  |  |  | Single_Ended | Single_Ended | Single_Ended | Voltage Output | Differential_Mode
Chasis Slot # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Channel
0 | Danf_QD_U1 | H_LN2_setpoint | MOT_V8_Open | Cl_N_open | PT100-N2_Supply | m_flow_LCL | LVDT_V6** (Q2) | CL_P_motor_setpoint | VT_I+U to VT_I+L
1 | Danf_QD_L1 | H_LHe_setpoint | MOT_V8_Close | CL_N_close | PT100-N2_Return | m_flow_RCL | LVDT_V8 | CL_N_motor_setpoint | VT_1/6 to VT_1/1
2 | Danf_QD_U2 |  | MOT_V6_Open | VWR_Open | PT100-Turret End | m_flow_neck | LVDT_V6 |  | VT_2/1 to VT_2/6
3 | Danf_QD_L2 |  | MOT_V6_Close | VWR_Close | PT100-Close End |  | LVDT_V4 |  | VT_3/6 to VT_3/1
4 | Danf_QD_U3 |  | MOT_V4_Open | Power_cycle_h_Lhe | PT100-Magnet Center |  | LVDT_V3 |  | VT_4/1 to VT_4/6
5 | Danf_QD_L3 |  | MOT_V4_Close | Power_cycle_h_LN2 | PT100-Close End |  | LVDT_V1 |  | VT_1/6 to VT_2/6
6 | Danf_QD_U4 |  | MOT_V3_Open | Constant Current Enable | PT100-He Supply |  | LVDT_V13 |  | VT_3/6 to VT_4/1
7 | Danf_QD_L4 |  | MOT_V3_Close | Penningvac_HV | PT100-He Return | m_flow_LCL_org | LVDT_V19 |  | VT_I-U to VT_I-L
8 | Danf_QD_Sum |  | MOT_V1_Open | Keep_Alive_Reset | PT100-N2_Outer Shield | m_flow_RCL_org | LVDT_CL_P |  | N/A
9 | Dump_switch_Timer |  | MOT_V1_Close | Keep_Alive_Control | PT100-N2_Inner Shield | m_flow_neck_rg | LVDT_CL_N |  | N/A
10 | Dump_switch_status |  | MOT_V13_Open | Dump_Switch_Relay | PT100-He Reservoir | p_He | VWR_Position |  | N/A
11 | Valve Mtrs KS remote |  | MOT_V13-Close | PLC_Fast_Relay | PT100-N2 Reservoir | p_N2 |  |  | N/A
12 | PSU_Control_Pwr_on |  | MOT_V19_Open | PLC_Slow_Relay | CG-1 | Pirani_Vac |  |  | N/A
13 | PSU_Main_Pwr_on |  | MOT_V19_Close | PSU_Reset | CG-2 | Penning_Vac | MPS_Current_Signal |  | N/A
14 | PSU_ready |  | CL_P_open | Dump_Switch_Reset | CG-3 | h_LN2 |  |  | N/A
15 | PSU_Sum_interlocks |  | CL_P_close | Danf_QD_Reset | CG-4 | h_LHe |  |  | N/A
Quad's Dataforth Signal Conditioner Table SCM5B modules
Rack | 1 | 2 | 3 | 4 | 5
Channel
1 | 34-1562 [RTD - +/-5V] | 34-1562 [RTD - +/-5V] | 43-05D [+/-5V - +/-5V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40V - +/-10V]
2 | 34-1562 [RTD - +/-5V] | 34-1562 [RTD - +/-5V] | 43-05D [+/-5V - +/-5V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40V - +/-10V]
3 | 34-1562 [RTD - +/-5V] | 34-1562 [RTD - +/-5V] | 43-05D [+/-5V - +/-5V] | 31-03D [+/-10V - +/-10V] | 31-09D [+/-40V - +/-10V]
4 | 34-1562 [RTD - +/-5V] | 34-1562 [RTD - +/-5V] |  | 31-03D [+/-10V - +/-10V] | 31-09D [+/-40V - +/-10V]
5 | 34-1562 [RTD - +/-5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 31-09D [+/-40V - +/-10V]
6 | 34-1562 [RTD - +/-5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 31-09D [+/-40V - +/-10V]
7 | 34-1562 [RTD - +/-5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 31-09D [+/-40V - +/-10V]
8 | 34-1562 [RTD - +/-5V] |  | 30-02D [+/-50mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]

## HMS Dipole
Dipole's PLC I/O Usage Table
Module | IV16 | OW16I | OW16I | OW16I | IF16 | IF16 | IF16 | IF16 | IF16
Configuration |  |  |  |  | Single_Ended voltage | Single_Ended Current | Single_Ended Voltage/Current | Single_Ended Voltage | Differential_Mode Voltage
Chasis Slot # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Channel
0 | Danf_QD_U1 | MOT_JTV12_Close | MOT_JTV1_Open | MOT_JTV9_Open | T_He_LCLW | m_flow_LCL | T_HX_He |  | VT_1_a to VT_2_a
1 | Danf_QD_L1 | MOT_JTV12_Open | MOT_JTV1_Close | MOT_JTV9_Close | T_He_RCLW | m_flow_RCL | LVDT_JTV1 |  | VT_3_a to VT_4_a
2 | Danf_QD_U2 |  | MOT_JTV2_Open | MOT_JTV10_Open | T_LN2_1 | Warm_Return_Position | LVDT_JTV2 |  | VT_5_a to VT_6_a
3 | Danf_QD_L2 |  | MOT_JTV2_Close | MOT_JTV10_Close | T_LN2_2 |  | LVDT_JTV3 |  | VT_7_a to VT_8_a
4 | Danf_QD_U3 |  | MOT_JTV3_Open | Warm_return_Open | T_LN2_3 | h_LN2 | LVDT_JTV4 |  | VT_9_a to VT_10_a
5 | Danf_QD_L3 |  | MOT_JTV3_Close | Warm_return_Close | T_LN2_4 |  | LVDT_JTV5 |  | VT_11_a to VT_12_a
6 | Danf_QD_U4 |  | MOT_JTV4_Open | h_Lhe_Current_enabled | T_LN2_IN |  | LVDT_JTV6 |  | VT_13_a to VT_14_a
7 | Danf_QD_L4 |  | MOT_JTV4_Close | Penning HV | T_LN2_OUT |  | LVDT_JTV7 |  | VT_15_a to VT_16_a
8 | Danf_QD_Sum |  | MOT_JTV5_Open | Keep_Alive_Reset | T_LHe_1 |  | LVDT_JTV8 | F_R1 | N/A
9 |  |  | MOT_JTV5_Close | Keep_Alive_Control | T_LHe_2 |  | LVDT_JTV9 | F_L1 | N/A
10 |  |  | MOT_JTV6_Open | NMR_Pwr | T_LHe_3 | p_He | LVDT_JTV10 | F_R2 | N/A
11 | JVT Mtrs KS remote |  | MOT_JTV6-Close | PLC_Fast_Relay | T_LHe_4 | p_N2 | T_HX_N2 | F_L2 | N/A
12 | PSU_Control_pwr_on |  | MOT_JTV7_Open | PLC_Slow_Relay | T_LHe_IN | Themo_Vac | LVDT_JTV12 | F_R3 | N/A
13 | PSU_Main_pwr_on |  | MOT_JTV7_Close | PSU_CPU_Reset | T_LHe_OUT | Penning_Vac | MPS_Current_Signal | F_L3 | N/A
14 | PSU_ready |  | MOT_JTV8_Open | PSU_diodes_Reset | T_LHe_LCLC | T_transfer_N2 |  | F_R4 | N/A
15 | PSU_Sum_Interlocks |  | MOT_JTV8_Close | Danf_QD_Reset | T_LHe_RCLC | h_LHe |  | F_L4 | N/A
Dipole's Datafroth Signal Conditioner Table SCM5B modules
Rack | 1 | 2 | 3 | 4 | 5 | 6
Channel
1 | 34-1562 [RTD - +/- 5V] | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
2 | 34-1562 [RTD - +/- 5V] | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
3 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
4 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
5 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
6 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
7 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
8 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]

## Rotation
Rotation's PLC I/O Usage Table
Module | OW16I | IB16D | IB16D | OB16D | OB16D | OF6VI | HSC | IF16
Configuration | Relays | Switches | Selector Switches | DC for Lights | LED display | MTR drive Voltages | High Speed Counters | Thumb Wheel Input
Chasis Slot # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Channel
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
Dipole's Datafroth Signal Conditioner Table SCM5B modules
Rack | 1 | 2 | 3 | 4 | 5 | 6
Channel
1
2
3
4
5
6
7
8