|  | 2005 |
| --- | --- |
|  | JLAB Lassiter / Pappal |

HMS PLC Documentation

Manual for the PLC control of the HMS magnets and the rotation of the HMS and SOS

CONTENTS

- Over View

- PLC

- Hardware & Instrumentation

3.1 Temperature Sensors

  - Thin-film-Carbon Glass sensors

  - Location of the thin-film Carbon Glass temperature sensors

  - Method of the thin-film Carbon Glass temperature sensors

  - Charts representing Temperature vs. Resistance curves

  - Thin-film Carbon Glass temperature sensors tags

  - PT 100

  - PT 100 temperature calculation

    - PT 100 temperature sensor

  - Location of PT100 sensors

  - Method of PT100 measurements

- Pressure & Vacuum

  - Helium and Nitrogen pressure measurement

    - Pressure sensors

  - Location of Pressure sensors

  - Method of Pressure measurement

  - Vacuum pressure measurement

    - Vacuum pressure sensors

    - Location of Vacuum pressure sensors

- Support Link Forces

  - Strain gauge sensors

  - Location of strain gauge sensors

  - Method of strain gauge measurement

    - Calculation of the forces from tension links

- Control Valves

  - Control devices of the Valve actuators

    - Linear Variable Differential Transducers

    - Electric Linear Actuator Drive motors

  - Location of Valve Actuators

  - Method of Valve Positional control

  - Adjustment of LVDT

    - Mechanical adjustments of the end switch

    - Adjustment of the LVDT

  - Variable tag information

- Flow Level

  - Mass-flow sensors

  - Location of Mass flow sensors

  - Method of mass flow measurement

  - Variable tag information

- Cool Down

  - Helium cool down logic

  - Helium warm up logic

  - Nitrogen cool down logic

  - Variable tag information

- NMR/PSU

  - NMR communications

  - Method of NMR/PSU measurement

  - Variable tag information

- Interlock

9.1 Variable tag information

- Voltage sensors

  - Location of Voltage sensors

  - Method of Voltage tap measurement

  - Variable tag information
1	Temperature Sensors

1.1	Thin-Film Carbon Glass Temperature Measurement (80K to 4K)

The Thin-Film Carbon Glass (CG) sensors are used to monitor the Helium temperatures in the following locations:

- The helium space of the cyro-can reservoir (CCR).

- Helium inlet and outlet tubes of the Magnet.

- Cold Mass of the Magnet.

- Cold end of the current leads.

The CG sensors are used in areas of moderate to high magnetic fields.  There are 8 sensors (along with their redundant counterparts) in the Magnet. These CG sensors are inversely, nonlinear and monotonic in their resistance vs temperature characteristics between 1.0 Kelvin and 300 Kelvin and have a fast response time of 0.5 ms for mK variations. The resultant magnetic field dependence is quite weak

dT<= -(5.46 + 0.03) B  1.62 + 0.02  mK up to 7.4 T)

CG sensors are insensitive to nuclear radiation.

dT + 30 mK at 4.2 K after 10 Mgy

A constant current source of 10 uA will be used to excite the sensors. The CG sensors have calibrated data from 4.2 Kelvin ( -269C) to 300 Kelvin ( 27C). Each sensing element has its own discrete resistance-temperature characteristic.

Table 1 Thin Film Carbon Glass Sensors Properties

| Type | Thin-Film-Carbon-Sensor |
| --- | --- |
| Temperature | <0.1 K to 300 K |
| Reproducibility | mK’s at 4.2 K after 1 yr |
| Stability | +3mK at 4.2 K |
| Dimensions (L x W x H) | 6 x 3 x 0.5 mm |
| Resistance (Typical) | 50  + 10% at 300 K 100  + 15% at 77K 1K + 20 % at 4.2 K |

1.2     Location of the Thin-Film-Carbon-Sensors

All CG sensors are placed on specially designed adapters in inaccessible locations. For this reason there are provided redundant sensors. The redundant sensors are marked with ‘r’ after designation of sensor (for instance T_Lhe_1 is type of sensor and T_Lhe_1r is type of redundant sensor). See Schematic drawing ###-##-#### for sensor locations.

Position of thin-film-carbon sensors:

T_LHe_1(T_LHe_1r)	inside the bobbin near corner # 1

T_LHe_2(T_LHe_2r)	inside the bobbin near corner #2

T_LHe_3(T_LHe_3r)	inside the bobbin near corner #3

T_LHe_4(T_LHe_4r)	inside the bobbin near corner #4

T_LHe_IN (T_LHe_INr)	liquid helium inlet tube in the supply tube

T_LHe_OUT (T_LHe_OUTr)	liquid helium outlet tube in the supply tube

T_Lhe_LCLC	on the cold end of the left current lead

T_Lhe_RCLC	on the cold end of the right current lead

1.4	Method of Thin-Film-Carbon Temperature Measurement

A constant current source of 10 uA is used to induce a measurable temperature dependent voltage across the CG sensor. The voltage across the sensor ranges from ~0.5 mV (300K) to ~10 mV (4.2K). This small voltage is then conditioned and amplified by a Dataforth SCM5B30-02D conditioner with a gain of 10Vdc/50mV.  The amplified signal is then fed into a 1756-IF16 input module where the voltage is converted back into a resistance measurement via the linear front end calibration of the 1756-IF16 module.

IF16 Front end calibration:

Input range: 0 V to 5.125 V,  Resolution (80uV/cnt) 16 bits.

Front end Calibration: 0 to 2.5 V    is 0 Ohms to 1250 Ohms (0.04 Ohms/cnt)

Table 2 Typical CG sensor front end calibration and resolution.

| Temperature | Resistance | mV at 10uA | Amplified Voltage 10V/50mV | Front end Calibration Ohms | Resolution mK/cnt |
| --- | --- | --- | --- | --- | --- |
| 300 | 50 | 0.5 | 0.1 | 50 | 2,400 |
| 77 | 100 | 1.0 | 0.2 | 100 | 308 |
| 4.2 | 1,000 | 10 | 2.0 | 1,000 | 1.7 |

Each CG sensors is calibrated, as is its current source, Dataforth’s signal amplifier and PLC module.  The 1756-IF16 module also provides 60 Hz normal mode noise rejection, voltage offset and Digital Filtering of Signal.

Table 3Table 1.2 Calibration table for the thin-film Carbon Glass Temperature sensors for the Dipole Magnet.

|  | Temperature | CG_1 | CG_1r | CG_2 | CG_2r |
| --- | --- | --- | --- | --- | --- |
| No | [K] | [] | [] | [] | [] |
| 1 | 300 | 50.2 | 54.7 | 53.8 | 54.6 |
| 2 | 250 | 54.5 | 59.7 | 58.9 | 59.3 |
| 3 | 200 | 60.8 | 65.6 | 64.5 | 64.5 |
| 4 | 150 | 68.9 | 74.7 | 73.8 | 73.5 |
| 5 | 100 | 82.1 | 88.3 | 87.3 | 85.6 |
| 6 | 77.35 | 93.4 | 100 | 99.2 | 97.6 |
| 7 | 50 | 115.1 | 119.7 | 118 | 111.3 |
| 8 | 20 | 166.8 | 165.3 | 159.3 | 136.4 |
| 9 | 10 | 391.6 | 371.6 | 380.5 | 363 |
| 10 | 5.2 | 907.8 | 889.4 | 980.6 | 925 |
| 11 | 4.2 | 1163.2 | 1165.325 | 1208.525 | 1208.525 |

##### Table 1.3 Calibration table for the thin-film carbon Temperature sensors

|  | Temperature | CG_3 | CG_3r | CG_4 | CG_4r |
| --- | --- | --- | --- | --- | --- |
| No | [K] | [] | [] | [] | [] |
| 1 | 300 | 50 | 50.2 | 54.7 | 50 |
| 2 | 250 | 54.5 | 54.7 | 60 | 54.4 |
| 3 | 200 | 61 | 61.1 | 66 | 60.6 |
| 4 | 150 | 69.4 | 69.3 | 75.5 | 67.4 |
| 5 | 100 | 83.7 | 82.8 | 89.4 | 82.7 |
| 6 | 77.35 | 94.9 | 93.7 | 101.3 | 93.7 |
| 7 | 50 | 117.1 | 115.1 | 120.8 | 115.8 |
| 8 | 20 | 171.2 | 170.5 | 162.3 | 171.5 |
| 9 | 10 | 389.8 | 367.8 | 392 | 392.5 |
| 10 | 5.2 | 885.8 | 836.1 | 938.3 | 930.6 |
| 11 | 4.2 | 1130.35 | 1081.4 | 1211.025 | 1214.75 |

##### Table 1.4 Calibration table for the thin-film carbon Temperature sensors

|  | Temperature | CG_In | CG_Inr | CG_Out | CG_Outr |
| --- | --- | --- | --- | --- | --- |
| No | [K] | [] | [] | [] | [] |
| 1 | 300 | 49.3 | 48.5 | 49.5 | 51.7 |
| 2 | 250 | 53.9 | 53.4 | 54.2 | 56.4 |
| 3 | 200 | 59.8 | 59.6 | 60.2 | 62.2 |
| 4 | 150 | 68.2 | 68.5 | 68.9 | 71.1 |
| 5 | 100 | 81.1 | 81.6 | 82.2 | 84.2 |
| 6 | 77.35 | 90 | 91 | 92.3 | 93.9 |
| 7 | 50 | 106.7 | 107.4 | 111.7 | 112.8 |
| 8 | 20 | 146.1 | 141.3 | 155.7 | 160.5 |
| 9 | 10 | 381.8 | 370.1 | 386.7 | 361.9 |
| 10 | 5.2 | 993.2 | 924.1 | 931.1 | 857.9 |
| 11 | 4.2 | 1321.35 | 1202 | 1202.175 | 1120.4 |

##### Table 1.5 Calibration table for the thin-film carbon Temperature sensors

|  | Temperature | CG_LCLC | CG_LCLCr | CG_RCLC | CG_RCLCr |
| --- | --- | --- | --- | --- | --- |
| No | [K] | [] | [] | [] | [] |
| 1 | 300 | 48.6 | 48.052 | 49.1 | 48.46 |
| 2 | 250 | 55 | 54.4 | 55.4 | 54.5 |
| 3 | 200 | 61.2 | 62.617 | 61.5 | 61.3 |
| 4 | 150 | 70.5 | 69.9 | 70.3 | 70.2 |
| 5 | 100 | 84.9 | 87.777 | 87.5 | 89.104 |
| 6 | 77.35 | 98 | 96 | 98.3 | 97.8 |
| 7 | 50 | 122.4 | 119.6 | 122.8 | 122.3 |
| 8 | 20 | 211.4 | 205.2 | 210.6 | 212.8 |
| 9 | 10 | 362.3 | 347.972 | 355.3 | 357.617 |
| 10 | 5.2 | 656.4 | 636.9 | 638.96 | 651.892 |
| 11 | 4.2 | 806.1 | 788.8 | 778.4 | 806 |

1.5	Charts representing Temperature vs. Resistance Curves

Figures 1 thru 4 show a typical CG temperature vs. resistance curve. Figure 1 is over the entire operation range of the sensor. Figures 2 thru 4 show the break up of the original data into three segments that were then fitted. Data for all the CG sensors can be found in the excel spreadsheet C\PLC\Dipole\Dipole_CG_Temperture.xls on Skylla’s hard drive.

1.6	Thin-Film Carbon Temperature sensors Tags

In the program Thin-Film-Carbon sensors are represented by a ‘tag’, which is a memory space in the PLC. Listed below are the CG sensor variables tags and their description.

| ### Variable | ### Description |
| --- | --- |
| T_Lhe_1 to T_Lhe_4 | Dipole:5:I.Ch8Data to Dipole:5:I.Ch11Data |
| T_Lhe_In | Dipole: 5:I.Ch12Data |
| T_LHe_Out | Dipole: 5:I.Ch13Data |
| T_LHe_L_CL_C | Dipole: 5:I.Ch14Data |
| T_LHe_R_CL_C | Dipole: 5:I.Ch15Data |
| CG_high_value | 1230 |
| CG_Low_value | 40 |
| CG_IN_High_value | 1325 |
| CG_CL_High_value | 900 |
| T_Lhe_1error to T_Lhe_4error T_Lhe_Ierror T_Lhe_Oerror T_Lhe_Lerror T_Lhe_Rerror Carbon_error | Warning Outputs Warm Up error |

2	PRESSURE

The pressure measurement includes the measurement of the nitrogen pressure, the helium pressure and the vacuum pressure in the HMS dipole magnet and in the reservoir.

  - Helium and Nitrogen Pressure measurement

    - Pressure Sensors

The pressure of helium and nitrogen will be measured with absolute pressure transducers of type P6P/5bar from Hottinger Baldwin Metechnik GmbH. The sensing element consists of a membrane with thin film strain gauge application in a full bridge circuit.

| Type | P6P/%bar |
| --- | --- |
| Principle of sensor | 1 K full bridge (string gauges) |
| Class of accuracy | 0.2 |
| Measurement range | 5 bar |
| Characteristics at 5 bar | 2mV/V |
| Natural freq. Of membrane | 9 kHz |
| Temperature range | -40 to +100  C |
| Pressure range (T=23 C) | 0 to 130 % |
| Overload Pressure (T=23 C) | 10 bar |
| Supply voltage of full bridge | 2.5 V to V |

Table 2.1: Characteristics of the P6P/5 bar pressure sensor

2.2	Location of Pressure Sensors

The pressure sensor of type P6P/5bar, for measuring the helium pressure, is placed on the top plate of the reservoir. Via a capillary tube the sensor detects the pressure in the liquid helium supply line. In the description and schematics the helium pressure valve is labeled p_He.

Similarly the pressure sensor of type P6P/5bar, for measuring the nitrogen pressure, is placed on the top plate of the reservoir. Via a capillary tube the sensor detects the pressure in the liquid nitrogen supply line. In the description and schematics the nitrogen pressure value is labeled p_N2.

  - Method of Pressure Measurement

The signal from Combivac CM-31, controller for the vacuum gauges, is brought in to the 1756-IF16 and its front end calibration is:

Front end calibration:

P_He: Dipole:6:I.Ch10Data

Input range: -10 V to 10 V

Calibration: 0 to 3.3 V    is 0 to -1302

P_N2: Dipole:6:I.Ch11Data

Input range: -10 V to 10 V

Calibration: 0 to 3.1 V    is 0 to -1255

Thermo_x:  Dipole:6:I.Ch12Data

Input range: 0 V to 10 V

Calibration: 0 to 10 V    is 0 to 10

Penning_x:  Dipole:6:I.Ch13Data

Input range: 0 V to 10 V

Calibration: 0 to 10 V    is 0 to 10

  - Vacuum Pressure Measurement

    - Vacuum Pressure Sensors

The vacuum pressure measurement occurs with two vacuum gauge heads from Leybold AG. The THERMOVAC gauge head TR201KF is used for the measurement of the absolute pressures in the rough and fine vacuum range. The actual pressure-sensing element within the gauge head is a tungsten filament.

| Type | THERMOVA TR201KF |
| --- | --- |
| Measurement range | 10 –3 to 103 mbar |
| Measurement filament | Tungsten |
| Temperature range | 0 to 40  C |
| Filament Temperature | 110  C |
| Max ambient temperature | 65  C |

Table 2.2: Characteristics of the THERMOVAC gauge head TR201 KF

The range between 10 –9 to 10 –2  mbar will be measured with a PENNIGVAC gauge head PR35. The actual measurement chamber of the gauge head contains the anode ring with the anode pin and the cathode plate.

| Type | PENNINGVAC PR35 |
| --- | --- |
| Measurement range | 10 –9 to 10 –2 mbar |
| Supply voltage | 3.3 kV |
| Nominal temperature | 80  C |
| Max ambient temperature | 65  C |

Table 2.3: Characteristics of the PENNINVAC gauge head PR35

    - Location of Vacuum Pressure Sensors

Both, the THERMOVAC gauge head TR201KF and the PENNINGVAC gauge head PR35, to detect the vacuum pressure p_Vac, are placed on the lateral area of the reservoir.

2.4.3	 Method of Vacuum Pressure Measurement

Thermovac:

Ua = 10/6 (log p + 3)

Ua: volts

P: mbar/Torr

P = 10 (0.6 Ua –3)

Penningvac:

Ua = 10/7 (log p + 3)

Ua  : volts

P   : mbar/Torr

p = 10 (0.6 Ua –3)

| Variable | Description |
| --- | --- |
| Thermo _X | Dipole: 6:I. Ch12Data |
| Penning_X | Dipole: 6:I. Ch13Data |
| P_he | Dipole: 6:I. Ch10Data |
| P_N2 | Dipole: 6:I. Ch11Data |
| P_vac | Output |
| P_vac_error | Warning output (Not (switch) and Thermo_error) or (switch and Penning_error) |
| Vac_switch | -2398 = 10(2398/1000) = 4* 10 -3 mbar |
| Thermo_min | -2900 = 10 –2,9= 1.259* 10 –3 mbar |
| Thermo_max | 2900 = 10 2,9= 794.3 mbar |
| Penning_min | -8900 = 10 -8.9= 1,259 10 –9 mbar |
| Penning_max | -2100 = 10-2,1= 7.94 10 –3 mbar |
| Thermo_error | [Value of Thermovac (connector)< Thermo_min) or (Value of Thermovac (connector) > Thermo_max] |
| Penning_error | [Value of Penningvac (connector)< Penning_min) or (Value of Penningvac (connector) > Penning_max] |
| P_He_error | Output warning (P_He < 0) or (p_He> p_He_max) |
| P_N2_error | Output warning (p_N2<0) or (p_N2 > p_N2_max) |

Table 2.4: Variable tags and description

3	FORCES

The strain gauge measurement includes the force measurement of strain studs in the tension links.

  - Strain Gauge Sensors

The constantan strain gauges CEA-06-125UT-350 are strain gauges with wire lattice in two directions.

| Type | CEA-06-125UT-350 |
| --- | --- |
| Temperature range | 100 C to 400C |
| Strain Limits | Approx. 5% of strain length |
| Nominal Resistance | 350.0 + 0.4 % |
| Gauge Factor (at 24C) | 2.11 + 1.0 % |
| Transverse sensitivity (at 24C) | (+0.7 + 0.2%) |

Table 3.1: Characteristics of the strain gauge sensors

  - Location of Strain Gauge Sensors

The strain gauge sensors are placed in the strain studs of the support links. Each strain stud is equipped with four strain gauges across the circumference at distances of 90. Two opposite strain gauges in a strain stud are connected to a full bridge circuit and measure the stress of the link.

Position of the strain gauge sensors:

F_R1 (F_R1r): sensors on the right strain stud corner #1 of HMS dipole

F_L1 (F_L1r): sensors on the left strain stud corner #1 of HMS dipole

F_R2 (F_R2r): sensors on the right strain stud corner #2 of HMS dipole

F_L2 (F_L2r): sensors on the left strain stud corner #2 of HMS dipole

F_R3 (F_R3r): sensors on the right strain stud corner #3 of HMS dipole

F_L3 (F_L3r): sensors on the left strain stud corner #3 of HMS dipole

F_R4 (F_R4r): sensors on the right strain stud corner #4 of HMS dipole

F_L4 (F_L4r): sensors on the left strain stud corner #4 of HMS dipole

  - Method of the Strain gauge measurement

The forces measured from the tension links are brought in to the signal conditioner Dataforth SCM5B38-35D, after being processed is sent to 1756 IF16.

Front end calibration:

F_R1: Dipole:8:I.Ch8Data

Input range: -10 V to 10 V

Calibration: -9.99 to 10 V is 2.0 to -2.0

Sensor Offset: 0.5

F_L1: Dipole:8:I.Ch9Data

Input range: -10 V to 10 V

Calibration: -10.0 to 10 V is 1.99 to -1.99

Sensor Offset: 0.27

F_R2: Dipole:8:I.Ch10Data

Input range: -10 V to 10 V

Calibration: -10.0 to 10 V is 2.0 to -1.99

Sensor Offset: 0.39

F_L2: Dipole:8:I.Ch11Data

Input range: -10 V to 10 V

Calibration: -10.0 to 10 V is 1.99 to -1.99

Sensor Offset: 0.68

F_R3: Dipole:8:I.Ch12Data

Input range: -10 V to 10 V

Calibration: -10.0 to 10 V is 1.99 to -1.99

Sensor Offset: 0.58

F_L3: Dipole:8:I.Ch13Data

Input range: -10 V to 10 V

Calibration: -10.0 to 10 V is 1.99 to -1.99

Sensor Offset: 0.17

F_R4: Dipole:8:I.Ch14Data

Input range: -10 V to 10 V

Calibration: -10.0 to 10 V is 1.99 to -1.99

Sensor Offset: 0.34

F_L4: Dipole:8:I.Ch15Data

Input range: -10 V to 10 V

Calibration: -10.0 to 10 V is 2.0 to -1.99

Sensor Offset: 0.22

| Variable | Description |
| --- | --- |
| F_R1 F_R2 F_R3 F_R4 F_L1 F_L2 F_L3 F_L4 | Dipole:8:I.Ch8Data Dipole:8:I.Ch 10Data Dipole:8:I.Ch 12Data Dipole:8:I.Ch 14Data Dipole:8:I.Ch9Data Dipole:8:I.Ch11Data Dipole:8:I.Ch13Data Dipole:8:I.Ch15Data |
| F_R1_error to F_R4_error F_L1_error to F_L4_error | Warning output |
| F_error | Summary of the warnings |
| Weight | Output |
| Weight_min | 70kN |
| Weight_max | 90kN |
| Weight_error | Output warning |

Table 3.2: Variable tags and description

3.3.1	Calculation of the forces from the tension links

F_R1_error: = Sensor broken (fault on the channel) or (F_R1< 0(NULL)) or (F_R1 > F_max)

F_max: = 4500: = 45KN-warning level

Weight Calculation

In this weight calculation there are only the 8 forces from the tension links included. If there is a weight on the support posts the weight calculation will be wrong. This case is possible during cool down and excitation of the magnet.

Weight: = F_R1 + F_L1 * cos15 * cos27.8 + F_R2 + F_L2 * cos15 * cos1.3

D_1000				     D_1000

- F_R3 + F_L3 + F_R4 +F_L4 * cos15* cos17.1

D_1000

Weight_error: = (weight > weight_max) or (weight < weight_min) or F_error

4	PT100

The temperature measurement includes the measurement of nitrogen and helium and cooled parts of HMS dipole magnet as well as the temperature of the heat exchanger

  - PT-100 temperature calculation

This temperature measurement is used to monitor and control the temperature of

- Liquid nitrogen shield of the dipole magnet

- Nitrogen inlet and outlet tubes of the dipole magnet

- Warm end of current leads

- Nitrogen temperature of the heat exchanger

    - PT-100 Temperature Sensor

About 60 Kelvin, the temperature will be measured with platinum resistance thermometers. The temperatures of the nitrogen-cooled shield as well as the temperatures of the supply and return line are measured with sensors of the series P100/1515 from Merz Mefuhlertechnik GmbH. The platinum resistance thermometer is usable for sensing temperature between 53Kelvin and 1073 Kelvin.

| Type | P 100/1515 |
| --- | --- |
| Resistance at 273.15K | 100 |
| Type encapsulation | Ceramic |
| Temperature range | 53K to 1073 K |
| Self heating coefficient | 0.03 K/mW |
| Temperature coefficient | 0.00385 //K |
| Body length | 15 mm |
| Body diameter | 4.5 mm |
| Lead Length | 8 mm |
| Lead diameter | 0.4 mm |

Table 4.1: Characteristics of the PT 100 temperature sensor

  - Location of PT-100 sensors

Inside the cryostat the PT-100 sensors are placed on the nitrogen cooled shield, on the liquid nitrogen inlet tube, and on the nitrogen outlet tube. These sensors are mounted at places with difficult access. For this reason there are provided redundant sensors. Outside the cryostat PT-100 sensors are placed on the warm side of vapor cooled current leads. In the description, redundant sensors are marked with ‘r’ after designation of sensor (for instance T-LN2_1 is type of sensor and T_LN2_1r is type of redundant sensor).

Except the sensors on the warm side of the current leads all the PT-100 temperature sensors are mounted on special designed adapters. The sensor on the warm side of the current leads are PT-100 foil sensors and fixed in a clamp mounted and then mounted on the current leads.

Position of the PT-100 sensors:

T_LN2_1(T_LN2_1r)	sensors on the nitrogen shield near corner #1

T_LN2_2(T_LN2_2r)	sensors on the nitrogen shield near corner #2

T_LN2_3(T_LN2_3r)	sensors on the nitrogen shield near corner #3

T_LN2_4(T_LN2_4r)	sensors on the nitrogen shield near corner #4

T_LN2_IN(T_LN2_INr)	sensors on the nitrogen inlet tube in the supply tube

T_LN2_OUT(T_LN2_OUTr)sensors on the nitrogen outlet tube near corner #2

T_LHe_LCLW		sensor on the warm end of the left current lead

T_LHe_RCLW		sensor on the warm end of the right current lead

T_HX				sensor on the heat exchanger

4.3	Method of PT 100 measurements

All the platinum resistance thermometers series P 100/1515 are conform to IEC751 standard (class B)

The temperatures of the warm side of the vapor cooled current leads are measured with platinum-resistance-foil-temperature sensors of the series S651PDX24B TELEMETER ELECTRONIC GmbH. The platinum resistance thermometers are usable for sensing temperature between 233 Kelvin and 450 Kelvin

| Type | S651PDX24B |
| --- | --- |
| Resistance at 273.15K | 100 |
| Type encapsulation | Polymid |
| Temperature range | 233K to 450K |
| Temperature coefficient | 0.00385 //K |
| Body length | 8 mm |
| Body width | 8 mm |
| Lead Length | 900 mm |
| Lead diameter | AWG 30 |

Table 4.2: Characteristics of the PT 100 temperature foil sensor

The forces measured from the tension links are brought in to the signal conditioner Dataforth SCM5B38-35D, after being processed is sent to 1756 IF16.

Front end calibration:

T_He_L_CL_W: Dipole:5:I.Ch0Data

Input range: 0 V to 5V

Calibration: 0 to 5 V is 73.15 to 373.16

Digital Filter: 2500ms

T_He_R_CL_W: Dipole:5:I.Ch1Data

Input range: 0 V to 5 V

Calibration: 0 to 5 V is 73.15 to 373.15

T_LN2_1: Dipole:5:I.Ch2Data

Input range: 0 V to 5 V

Calibration: 0 to 5 V is 72.95 to 373.06

T_LN2_2: Dipole:5:I.Ch3Data

Input range: 0 V to 5 V

Calibration: 0 to 5 V is 72.95 to 373.06

T_LN2_3: Dipole:5:I.Ch4Data

Input range: 0 V to 5 V

Calibration: 0 to 5 V is 73.15 to 373.15

T_LN2_4: Dipole:5:I.Ch5Data

Input range: 0 V to 5 V

Calibration: 0 to 5 V is 73.15 to 373.15

T_LN2_In: Dipole:5:I.Ch6Data

Input range: 0 V to 5 V

Calibration: 0 to 5 V is 73.15 to 373.15

T_LN2_Out: Dipole:5:I.Ch7Data

Input range: 0 V to 5 V

Calibration: 0 to 5 V is 73.15 to 373.15

The nitrogen shield temperature and the heat exchanger temperature are brought in as 0-5V, which is then converted to read temperatures in K.

| Variable | Description |
| --- | --- |
| T_LN2_1 to T_LN2_4 T_LN2_In T_LN2_Out T_Hx | Output variables Dipole: 5:I. Ch2Data to Dipole: 5:I. Ch7Data |
| T_LN2_1error to T_LN2_4error T_LN2_Ierror T_LN2_Oerror T_he_error | Warning output |
| T_LN2_error | Summary of the nitrogen temperatures |
| Pt100_T_min | = 76K |
| Pt100_T_max | = 320K |
| Pt100_T_maxC | = 85K |
| Cd_LN2_level | LN2 level control status from Task CD |

Table 4.3: Variable tags and description

T_LN2_1error= (T_LN2_1 < Pt100_T_min) or (T_LN2_1 > Pt100_T_max) or Broken sensor

Current leads warm end temperature

| Variable | Description |
| --- | --- |
| T_He_L_CL_W T_He_R_CL_W | Dipole: 5:I. Ch0Data Dipole: 5:I. Ch1Data |
| T_He_Lerror T_He_Rerror | Warning output |

T_He_Lerror: = (T_He_L < PT100_CL_min) or (T_He_L < TP100_CL_max)

PT100_CL_off: = 273.2 K

PT100_CL_max:: = 305K 			High warning level

PT100_CL_min: = 250 K			Low warning level

- Control Valves

The valves are used for the control of the flow of liquid cryogens, cool down gas, and exhaust gas to and from the cryogenic system of the HMS dipole magnet. The valve actuators provide the positional control for the valves. Each valve actuator consists of a valve actuator support assemble, a Linear-Voltage-Differential-Transducer (LVDT), an electric linear actuator.

  - Control Devices of the Valve Actuators

    - Linear-Voltage-Differential-Transducers

A Linear-Voltage-Differential-Transducer (LVDT) is applied to indicate the seat position of a valve. An operator at the PLC has the capability of seeing any position from 0% (soft seat) to 100% (full open), and also negative percent valve position, which indicates the valve is fully seated.

The LVDT contains three galvanic separated coils. A magnetic stainless steel housing provides electromagnetic and electrostatic shielding. The lightweight core in the center bore of the cylindrical housing varies the electrical coupling between the coils, dependent of its position.

The LVDT core motion is the sum of stroke length and 1/16 inch seating motion of the motor mounting plate at the valve actuator assembly.

| Type | MHR 250 |
| --- | --- |
| Input Voltage | 3 V rms (nominal) |
| Frequency range | 400 Hz to 20 KHz |
| Temperature range | 220K to 420 K |
| Null voltage | <0.5 % full scale outpout |
| Housing material | AISI 400 |
| Housing dimensions: |  |
| Diameter | 9.53 mm |
| Length | 47 mm |
| Core dimensions: |  |
| Diameter | 2.75 mm |
| Length | 28.5 mm |

Table 5.1: Characteristics of the LVDT

    - Electric Linear Actuator Drive Motors

The valve actuator is capable of strokes up to 5/8 inch with a seating force of 200 pounds. The stroke speed is approximately 30 seconds full stroke with continuous drive.

| Type | SURA part #001 |
| --- | --- |
| Supply voltage | 24 Vdc |
| Current | 1.5 A |
| Power | 36 W |
| Dimensions (Actuator): |  |
| Length | Approx. 0.20 m |
| Width | Approx. 0.20m |
| Height | Approx. 0.25 m |

Table 5.2 Characteristics of the actuator drive motor

  - Location of Valve Actuators

The valve actuators for the JT valves are located on the top plate of the reservoir. The valve actuators for the current lead return gas are located on the lateral side of the reservoir.

Designation of the valves:

JTV1	JT control valve for liquid helium supply to the magnet during cool down.

JTV2	JT control valve for gaseous helium supply to the magnet during cool down.

JTV3	JT control valve for liquid nitrogen supply to the magnet during cool down.

JTV4	JT control valve for liquid nitrogen supply to the reservoir.

JTV5	JT control valve for liquid helium supply to the reservoir.

JTV6	JT control valve for cold helium gas return from the reservoir.

V_LCL	Valve for controlling the helium gas consumption through the left current lead.

V_RCL	Valve for controlling the helium gas consumption through the right current lead.

  - Method of Valve Positional Control

The LVDT halfbridge, via the Modular LVDT signal conditioner (LVC-2412), sends the control valve (true-valve) position to a 1756 IF-16 Allen Bradley module. In case of automatic control (switch in “Auto” position), the digital output signal activates the relay on the relay card for opening (or closing) the valve. The motor opens (or closes) the valve, until the deviation between the set-value and the true-value becomes a minimum.

In manual mode (switch in “Man” position), the operator can open (or close) the valve by pressing the switch on the front panel to the chosen position. The signals from the LVDT sensors are brought into a Macro sensor LVC-2402.

Front end calibration:

S1_LVDT_true to S9_LVDT_true: Dipole:5:I.Ch1Data to Dipole:5:I.Ch9Data

Input range: 0 mA to 20mA

Calibration: 4 to 20 mA  is -9 to 100

S10_LVDT_true: Dipole:5:I.Ch10Data

Input range: 0 mA to 20mA

Calibration: 0 to 20 mA  is 0 to 20

  - Adjustment of LVDT

    - Mechanical adjustments of the end switch

At all standard CEBAF valves the difference between opened and closed position is 9/16”. Both valves for the control of the current leads flow have a width of 7/16”. At first you have to set the screws at the limit switches of the valves so that the distance between the Softseat (0%) and full open (100%) is 9/16” (7/16”). This may be done with a caliper and the blue current controlled power supply from the valve tools.

    - Adjustment of the LVDT

The LVDT’s are measured with a ‘macrosensor’. For the current loop calibration, adjust the Zero control on the macrosensor for a loop current of 12mA. De-energize the module, after establishing the required connections, re apply DC power to the module, and move the LVDT’s core or body to read 12 mA. This position is the true null position of the sensor and the point from which subsequent measurements are made.

(Refer: Instruction Manual Low Voltage DC-Operated Modular LVDT Signal Conditioner Model LVC-2412)

  - Variable Tag information

| S1_LVDT_true to s9_LVDT_true | Valve position output Dipole:7:I.Ch1Data to Dipole:7:I.Ch9Data |
| --- | --- |
| S1_LVDT_fault to S9_LVDT_fault | Channel faults |
| S1_error to s9_error | Valve position warning |
| S_error | Summary warning output |
| S1_set to s9_set | Input from task VALVES |
| HMI_valvesManual | Key-switch position, input from HMI |
| Cd_Lhe_Level | Status Lhe level control from Task CD |
| T_he_error | Heat exchanger sensor warning from task PT100 |
| LVDT_max | 105% |
| LVDT_min | -10.5% |
| Ds_max | 5% Upper warning level |
| Ds_min | -5% Lower warning level |
| T_ds_maxN2 | 1200000 msecs Delay time for Nitrogen valves |
| T_ds_maxHe | 700000 msecs Delay time for Helium valves |
| Sec | 300msecs |

Table 5.3: Variable tags and description

- Flow Level

The mass-flow meters measures the vaporized helium flow through the pair of high current leads.

  - Mass-Flow sensors

The mass-flow meter, series MKS 0758A, is designed to provide accurate and repeatable control of gas flow. The mass-flow meter measured the flow by measuring the power required to maintain a pre-established temperature profile along a laminar flow sensor tube.

Upon entering the flow meter, the gas stream is divided into two parallel paths. The first path is directed through the sensor tube, the second goes through the changeable bypass. The two paths provide a length to diameter ratio of greater than 100:1 assuring laminar flow.

In the flow-meter, resistance heaters are wound on the sensor tube and form the active legs of bridge circuits. Their temperatures are established so that a voltage change on the sensor winding is a linear function of a flow change, This signal is then amplified to provide a 4 to 20 mA output.

| Type | MKS 758-100L-RK |
| --- | --- |
| Full scale range ( for nitrogen) | 100 slm |
| Accuracy | 1.0% of F.S |
| Repeatability | +0.2 % of F.S |
| Resolution | +0.1 % of F.s |
| Operating temperature range | 288K to 413 K |
| Warm up time | 30 minutes |
| Maximum inlet pressure | 150 psig |
| Pressure Coefficient | 0.005 % reading/psi |
| Minimum pressure drop | 0.15 to 1.25 psid @ atm |
| Input Voltage at start-up | 400 mA |
| Output signal | 4 to 20 mA |
| Isolation voltage | 1500 volts |
| Leak integrity | < 10-9 scc/sec (helium) |

Table 6.1 Characteristics of the MKS mass-flow meter

The operation of the mass-flow meters was checked with gaseous helium at 290 Kelvin.

  - Location of Mass-Flow sensors

Each vapor cooled current lead has its own helium gas return pipe. For measuring the gas flow though the current leads, mass-flow meters are built-in the helium gas return pipes behind the control valves. The mass-flow meters MLS 0785A are located on the lateral area of the reservoir. They indicate the mass-flows m_flow_LCL and m_flow_RCL.

  - Method of Mass_Flow measurement

For powering the resistance heater, the MKS 0785Z mass-flow meters are supplied by an external 24 Vdc power supply. The mass-flow meters send a flow dependent current output signal to the Signal Conditioner.

The control program generates the flow value by consideration of the gas correction factor for helium (GCF He). The GCF He  is a function of specific heat, density, and the molecular structure of the gas. If nitrogen is the baseline gas, the GCF He is determined by using the following equation:

GCF He  = N2  . CpN2  . SHe 					N2    = 1.250 g/l				He   . CpHe					CpN2  = 0.2485 cal/g.K

He    = 0.1786 g/l

CpHe = 1.241 cal/g.K

SHe   = 1.030

GCF He = 1.4435

X		Density of gas x

CpX		Specific heat of gas x

SX		Molecular structure correction factor for monatomic gas X.

To calculate the mass-flow value of helium, use the following equation:

mHe = mN2

GCF He

Front end calibration:

m_flow_Lx and m_flow_Rx : Dipole:6:I.Ch0Data and Dipole:6:I.Ch1Data

Input range: 0 mA to 20mA

Calibration: 4 to 20 mA is 0 to 8300

I_coarse: Dipole:7:I.Ch13Data

Input range: 0V to 10V

Calibration: 0 to 10 V is 0 to 3000

6.5 Variable tag information

| Variable | Description |
| --- | --- |
| M_flow_Lx M_flow_Rx | Dipole: 6:I. Ch0Data Dipole: 6:I. Ch1Data |
| I_coarse | Dipole: 7:I. Ch13Data |
| Flow_increasing_factor | 1.2 |
| m_flow_max m_flow_min | 8325 l/h 84 l/h |
| M_flow_set | Set value for the mass flow unit [l/h] |
| h_LN2_error h_LHe_error | Sensor warning |
| M_flow_error | Summary of right and left mass flow sensor warning |
| h_LN2 h_Lhe | Nitrogen Level Unit [%] Dipole: 6:I. Ch14Data Helium level unit [%] Dipole: 6:I. Ch15Data |
| h_LHe_max h_LHe_min | 99 % 15% |
| h_LN2_max h_LN2_min | 99 % 20 % |
| T_LN2_error | Summary of the nitrogen temp. Warnings from task PT100 |
| T_LHe_error | Summary of the helium temp. Warnings from task CARBON GLASS |
| cd_Lhe_Level | Helium level control cooling status from task CD |
| P_He_Interlock | Helium pressure interlock |
| P_N2_Interlock | Nitrogen pressure interlock |
| Error | Summary of all warnings |
| P_Vac_error | Vacuum pressure warning |
| S_error | Summary of the LVDT sensor warnings from task LVDT |
| F_error | Summary of the forces warnings from task FORCES |
| cd_LN2_Level | Nitrogen level control cooling status |
| no24V_error | 24V supply warning |
| U_error | Summary of the voltage warnings from task VOLTAGE |
| RampCtrlErr | Ramp up and field control error from task NMR |
| a0_flow | 3340 l/h |
| a2_flow | 88 l/h |

Table 6.2: Variable tags and description

I_true = ADC_readback_MPS * 10 * 3000

999999

I_Max = The greater value between I_true and I_Coarse

M_flow_set: = [(( I_max )2  * a2_flow )+ a0_flow ] * Flow_increasing_factor

1000

Summary of mass flow warning

h_LN2_error: = (h_LN2 > h_LN2_max) or (h_LN2 < h_LN2_min)

h_Lhe_error: = (h_LHe > h_LHe_max) or (h_LHe < h_LHe_min)

7	Cool Down

In this task the set values for the values are calculated for all the cooling functions.

The main cooling functions are

- Cool-down

- Warm up

- Stand by

- Cooling error

The status cooling error shows that no cooling function is selected.

General Calculated values

T_LN2_max: = MAX (T_LN2_1, T_LN2_2, T_LN2_3, T_LN2_4)

T_LHe_max: = MAX (T_Lhe_1, T_Lhe_2, T_Lhe_3, T_LHe_4, T_LHe_In, T_LHe_Out)

T_LHe_min: = MIN (T_Lhe_1, T_Lhe_2, T_Lhe_3, T_LHe_4, T_LHe_In, T_LHe_Out)

T_Lhe_av: = (T_Lhe_1+T_Lhe_2+T_Lhe_3+T_Lhe_4) / 4

| Variable | Description |
| --- | --- |
| T_LN2_1 to T_LN2_4 T_LN2_1error to T_LN2_4error | Nitrogen shield temperatures and sensor warnings from task PT100 Dipole: 5:I. Ch2Data to Dipole: 5:I. Ch5Data Warning Outputs |
| T_LHe_1 to T_LHe_4 T_LHe_1error to T_Lhe_4error | Bobbin temperatures and sensor warnings from the task CARBON GLASS Warning outputs |
| T_He_Delta_2 | 70K (User defined limits) |
| T_He_Delta | 50K (User defined limits) |
| Delta_T3_W | Temperature range check |
| Delta_T1_W | Temperature range check |
| Delta_T2_W | Temperature range check |
| Delta_pipe | Difference between temperatures between inlet gas and average magnet temperature. |

Table 7.1: Variable tags and description

N2_error: = T_LN2_error or T_LN2_2error or T_LN2_3error or T_LN2_4error

He_error: = T_Lhe_1error or T_Lhe_2error or T_Lhe_3error or T_Lhe_4error

7.1	Helium cool down logic

The cool down of the magnet is worked in four steps. The cool down functions are

- Cool down with temperature controlled helium gas.

- Cool down the Lhe pipe

- Cool down the magnet with Lhe

- Lhe level control

It is possible to select one or more cool down functions. If all functions are selected the magnet will be cooled automatically. Make sure, that the warm helium return manual valve is open and the check valve opener is in close position during cool down.

| Variable | Description |
| --- | --- |
| T_Warm_gas T_pipe T_magnet T_Lhe_level | These bits are on if the temperatures of the magnet are in the range between the levels to switch |
| S_warm_gas | 85 K |
| T_S_pipe | 50 K (Temperature to start cooling cool-down pipe) |
| S_Level | 20 |
| Warm_up Stand_by Stop_cooldown | HMI input |
| Cool_down | Magnet is cooling down |
| Start_cd | HMI tag to start cool down |
| CD_Stop | Stops cool down, if HMI stops cool down or standbys, or if there is a warm up, or if there is a cool down error, |
| cd_error | Invalid status state. Cool down state is undetermined. |
| cd_pipe_enabled | HMI input |
| cd_LHe_Magnet_enabled | HMI input |
| cd_LHe_level_enabled | HMI input |
| Heat_exchanger_start | HMI input |
| cd_warm_gas cd_pipe cd_LheMagnet cd_LHe_level | Cool down status bits output |

Table 7.2: Variable tags and description

Fig 7.1: Helium cooldown state logic

7.2	Helium warm up logic

The warm up of the magnet is working in two steps.

The warm up functions are

- Warm up delay

- Warm up with temperature controlled helium gas

It is possible to select one or both warm up functions. If all functions are selected the magnet will be warmed automatically. Make sure, that the warm helium return manual valve is open and the check valve opener is in close position.

| Variable | Description |
| --- | --- |
| wu_delay wu_warm_gas | Status bits |
| cd_inhibit_O | Inhibit helium cooling from task CD_IN |
| T_cd | 10 ms |
| S_WU | 2500 = 250K Temperature level to switch off warm up |
| S_WU_max | 200K height level to switch between wu_delay and wu_warm_gas |
| Warm_up_completed |  |

Table 7.3: Variable tags and description

Fig 7.2: Helium warm up logic

7.3	Nitrogen Cool down logic

The cool down of the nitrogen shield is working in two steps. The nitrogen cooling functions are

- Cool down the shield with LN2

- LN2 level

The program selects automatically the nitrogen cooling function. In case of the main cooling functions cool down or stand by is selected the nitrogen cooling is active

| Variable | Description |
| --- | --- |
| H_LN2 | Dipole: 6:I. Ch14Data |
| cd_LN2 cd_LN2_level | Nitrogen cooling status bits |
| S_LN2_max | 100 = 100K |
| S_LN2_G2 | 20% |

Table 7.4: Variable tags and description

Fig 7.3: LN2 Standby

7.4	Variable tag information

| Variable | Description |
| --- | --- |
| V_close | -7 |
| V_open | 90 |
| S1_pipe S2_pipe | Set point from pipe cooldown, PID controller |
| S1_auto S3_auto S5_auto S6_auto S7_auto S8_auto | Auto position for cool down LHe magnet. |
| S1_max to S10_max | Set point from max flow PID loop controller. |
| S1_min to S10_min | Minimum valve position for auto control |
| S1_set | Valve set position for auto control, set point of POSP_JT1 |
| S2_set | Valve set position for auto control, set point of POSP_JT2 |
| S3_set | Valve set position for auto control, set point of POSP_JT3 |
| S4_set | Valve set position for auto control, set point of POSP_JT4 |
| S5_set | Valve set position for auto control, set point of POSP_JT5 |
| S6_set | Valve set position for auto control, set point of POSP_JT6 |
| S7_set | Valve set position for auto control, set point of POSP_JT7 |
| S8_set | Valve set position for auto control, set point of POSP_JT8 |
| S9_set | Valve set position for auto control, set point of POSP_JT9 |
| S10_set | Valve set position for auto control, set point of POSP_JT10 |
| S11_set | Valve set position for auto control, set point of POSP_JT11 |
| Cd_pipe | Status bit for cool down pipe |
| Wu_pipe | Status bit for warm up pipe |
| S1_manual to S11_manual | Control bit to put valve in PLC manual mode. |
| S1_man_max to S11_man_max | Upper limit of valve in PLC manual mode. |
| S1_man_min to S11_man_min | Lower limit of valve in PLC manual mode. |
| S1_man to S11_man | Set point in manual mode HMI input. |
| PLC_control | Key switch bit, PLC control or local rack control |
| S1_pipe_P S2_pipe_P S1_max_P S2_max_P S5_max_P S5_P Sf_P_out S9_P_out S10_P | Proportional gain for PID |
| S1_pipe_I S1_pipe_I S1_max_I S2_max_I S5_max_I S5_I Sf_I_out S9_I_out S_10_I | Integral gain for PID |
| H_LN2_lower | 60 |
| CFI6711C | Helium 4.2 K flow to Hall C [g/s] |
| CEV6711C | Helium 4.2 K flow limit. ESR set point. |
| CEV6711C_Op | Helium 4.2 K flow limit. PLC limit |
| CFI6711C_LL | Helium 4.2 K flow lower limit. PLC limit Flow to hall should not drop below this value. |
| CFI60DLP |  |
| CFI60DLP_Limit |  |
| V_max |  |
| Valve_Cycle_time | Period of output pulse in seconds |
| Valve_Rate | Open/Close rate in %/second |
| JT_Max_On_Time | Maximum time in seconds that a open or close pulse can be on. |
| JT_Min_On_Time | Minimum time in seconds that a open or close pulse can be on. |
| JT1_open to JT11_open | Control bit to open valve |
| JT1_close to JT11_close | Control bit to close valve |
| h_LHe_set |  |
| T_TL_1 |  |
| T_Return_max |  |
| Set_s6_close |  |
| M_flow_L |  |
| M_flow_R |  |
| DTWarmGasOut | Temperature difference between bobbin temperature and helium inlet temperature |
| T_HX | Dipole:7:I.Ch0Data |
| T_HX_set |  |
| T_HX_LN2 | Dipole:7:I.Ch11Data |
| T_HX_LN2_set |  |
| BV_close | 0 |
| BV_open | 100 |

8	NMR/PSU

The NMR is used to regulate the magnetic field, communicate and control the power supply. RS232, and IEEE 488 ports, ASCII communications, on the NMR are used to talk to the Allen Bradley Flex I/O module and the MPS respectively. A custom made program for the Flex port, which was later modified was used at the software end.

  - Communications

The PLC uses the local control net, to communicate to the Flex I/O over its backplane, which talks to the NMR over its application port.

| Enabled | Yes |
| --- | --- |
| Type | 3 |
| Baud Rate | 2400 |
| Parity | None |
| Data Bits | 8 |
| Stop Bits | 1 |
| RTS On | 0 |
| RTS Off | 1 |
| Handshaking | None #None,RTS/CTS, DTR/DSR, XON/XOFF |
| Rx Term Char Count | 1 #0 to 12 characters to delimit end of message |
| Rx Term Characters | 13 |
| Rx Packet Length | 26 |
| Rx Message Timeout | 200 |
| Rx Intercharacter Delay | 30 |
| Rx Swap Bytes | No |
| Tx Message Timeout | 5000 |
| Tx Minimum Delay | 0 |
| Tx Swap Bytes | No |

Table 7.1: Configuration file of the Flex I/O port

  - Method of NMR/PSU measurement

Pro-Linx gateway, the manufacturers of the Flex I/O module, developed a prototype code for Jlab. This prototype was further enhanced to suit our needs. The code is in written using Function Block Diagrams and ladder logic. Function Block Diagrams (FBD), do not support ASCII communications, hence the need to use ladder logic. The commands that need to be sent out are triggered by the Human Machine Interface (HMI) that is interfaced in the FBD. The read back from the commands sent to the NMR and PSU are interpreted in the ladder logic.

In the main FBD, most of the commands that are sent out to the NMR/MPS are triggered by the HMI.

ASCII_Subroutine_1: The Flex port reads and writes every scan. This subroutine will process the data for the MVI94ASCII module only when a new block of data has been received from the module.  If there is not a new block pending, then the next subroutine will not be called.

ASCII_Subroutine_2: The first rung makes sure that only new blocks of data are processed. A bunch of commands that need to be sent out to the NMR and MPS, are placed in an array and are sent to the NMR and MPS, every “count”.

| Array element | Command |
| --- | --- |
| SString[1] | $03$r$l Command to take the NMR out of transparency. |
| SString[2] | Any command that needs to be sent to the NMR. |
| SString[3] | $05 Enquire command to read the NMR field display |
| SString[4] | S1 Reads internal instrument status. |
| SString[5] | S2 NMR signal status. |
| SString[6] | S3 Front panel status. |
| SString[7] | S4 DAC status |
| SString[8] | S5 Regulation status |
| SString[9] | S6 Alarm configuration status |
| SString[10] | S7 Alarm measurement status |
| SString[11] | $05 Enquire command. It is sent out again to read the display faster. |
| SString[12] | N$r$l Command to put the NMR in transparency mode, so the flex can communicate with the MPS. |
| SString[13] | Any command that needs to be sent to the MPS. |
| SString[14] | CMDSTATE$r Command to read the state of MPS, whether in REMOTE LOCAL LOCK |
| SString[15] | AD 0$r Command to |
| SString[16] | AD 2$r Command to |
| SString[17] | Has been left blank because to accommodate change in program. |
| SString[18] | AD 8$r Command to |
| SString[19] | RA$r |
| SString[20] | R3$r |
| SString[21] | S1$r |

The response from the MPS and the NMR are processed and stored in tags for later use. Two timers are responsible to keep track of any communication errors. If there is no response from the NMR/MPS the timers count up to the preset value and if not reset will set a communication error bit.

  - Variable tag information

| Variable | Description |
| --- | --- |
| Momentum_Input_HMI | Momentum input from HMI |
| ECL_value | Value from NMR |
| ECH_value | Value from NMR |
| B_Input_HMI | Field input from HMI |
| B_select_HMI | HMI input |
| B_True_NMR | Field value from NMR |
| B_Delta_min | .00008 |
| Dipole_Ready | Dipole is ready when set |
| HMI_Start_Excitation | HMI input |
| Regulation_Off | HMI input |
| Regulation_error |  |
| HMI_Stop_Excitation | HMI input |
| LR | Control bit |
| NMR_LR | Send command (bit) to NMR |
| PSU_Sum_Interlock | Sum of power supply interlocks |
| NMR_error | Bit indicating NMR signal lost and MPS not stable |
| PSU_Remote | Alias for MPS_cmd_state_Read.DATA[3] |
| NMR_EB | Send command (bit) to NMR |
| NMR_ER1 | Send command (bit) to NMR |
| ER0 | Send ER0 cmd to NMR |
| NMR_Field_not_found | Alias for NMR_Status[7].0 |
| NMR_Signal_Lost | Alias for NMR_Status[7].2 |
| MPS_not_stable | NMR_Status[7].3 |
| NMR_Lock | Alias for NMR_Status[1].5 |
| NMR_Task_Finished | NMR_Status[5].0 |
| HMI_NMR_ER1 | HMI input: Send ER1 |
| HMI_PSU_On | HMI input: Switch on MPS |
| RS_PSU_On | Reset bit |
| Set_value_MPS | Read back of MPS set value |
| ADC_readback_MPS | ADC read back of MPS |
| ADC_min | 500 |
| MPS_PowerOn | Send command (bit) to NMR |
| HMI_PSU_Off | HMI input: Switch off MPS |
| RS_PSU_Off | Reset bit |
| MPS_PowerOff | Send command (bit) to NMR |
| HMI_Start_ECL | HMI input |
| HMI_BI_Lowpt | HMI input |
| HMI_BI_Highpt | HMI input |
| HMI_ECL_value | ECL value calculated from HMI input |
| NMR_ECL | ECL value calculated from HMI input |
| Alarm_in_6 | Alias for NMR_Status[5].1 |
| Alarm_in_7 | Alias for NMR_Status[5].2 |
| ECL_error | Error bit |
| ECL_Done | Reset bit |
| RS_Start_ECL | Reset bit |
| HMI_Set_Current_St | HMI input |
| RS_set_current | Reset bit |
| HMI_Start_ECH | HMI input |
| NMR_ECH | Send command (bit) to NMR |
| HMI_ECH_value | ECH value calculated from HMI input |
| ECH_error | Error bit |
| RS_Start_ECH | Reset bit |
| HMI_Start_ECS | HMI input |
| HMI_ECS_value | ECS value calculated from HMI |
| NMR_ECS | Send command (bit) to NMR |
| ECS_error | Error bit |
| ECS_Done | Reset bit |
| RS_Start_ECS | Reset bit |
| HMI_PSU_Reset | HMI input: Reset MPS |
| RS_PSU_Reset_Off | Rest bit |
| MPS_Reset_interlocks | Send command (bit) to NMR |
| HMI_Manual_EB | HMI input: Field value from HMI |
| NMR_Man_EB | Send command (bit) to NMR |
| HMI_Search_On | HMI input |
| NMR_Field_Search_On | Send command (bit) to NMR |
| HMI_Search_Off | HMI input |
| NMR_Field_Search_Off | Send command (bit) to NMR |
| HMI_Polarity_Neg | HMI input |
| MPS_PO_Neg | Send command (bit) to MPS |
| RS_Pol_Neg | Reset bit |
| HMI_Polarity_Pos | HMI input |
| MPS_PO_Pos | Send command (bit) to MPS |
| RS_Pol_Pos | HMI input |
| MPS_current_send | Send command (bit) to MPS |
| MPS_Wa | Current value calculated. |
| HMI_NMR_Remote | HMI input |
| NMR_R | Send command (bit) to NMR |
| HMI_NMR_Local | HMI input |
| NMR_L | Send command (bit) to NMR |
| HMI_NMR_DisplayT | HMI input |
| NMR_DisplayT | Send command (bit) to NMR |
| HMI_NMR_Auto | HMI input |
| NMR_Auto | Send command (bit) to NMR |
| HMI_NMR_Manual | HMI input |
| NMR_Manual | Send command (bit) to NMR |
| HMI_NMR_POP | HMI input |
| NMR_POLP | Send command (bit) to NMR |
| HMI_NMR_PON | HMI input |
| NMR_POLN | Send command (bit) to NMR |
| HMI_NMR_Speedwrite | HMI input |
| NMR_Speedwrite | Send command (bit) to NMR |
| HMI_NMR_Integral_Coeff | HMI input |
| NMR_Integral_Coeff | Send command (bit) to NMR |
| HMI_NMR_Mux_write | HMI input |
| NMR_Mux_write | Send command (bit) to NMR |
| HMI_NMR_Mux_range_write | HMI input |
| NMR_Mux_range_write | Send command (bit) to NMR |
| HMI_MPS_Soff | HMI input |
| MPS_SOff | Send command (bit) to MPS |
| HMI_MPS_Rem | HMI input |
| MPS_Rem | Send command (bit) to MPS |
| HMI_MPS_Goff | HMI input |
| MPS_Goff | Send command (bit) to MPS |
| HMI_MPS_Ulock | HMI input |
| MPS_Ulock | Send command (bit) to MPS |
| HMI_MPS_Local | HMI input |
| MPS_Local | Send command (bit) to MPS |
| HMI_NMR_ER0 | HMI input |
| NMR_ER0 | Send command (bit) to NMR |
| HMI_MPS_Slew_write | HMI input |
| MPS_Slew_write | Send command (bit) to MPS |
| HMI_NMR_Reset | HMI input |
| NMR_Reset | Send command (bit) to NMR |
| HMI_NMR_EFC_write | HMI input |
| NMR_EFC_write | Send command (bit) to NMR |
| HMI_NMR_Write_Settlingtime | HMI input |
| NMR_Write_Settlingtime | Send command (bit) to NMR |
| HMI_MPS_ERRC_write | HMI input |
| MPS_ERRC_write | Send command (bit) to MPS |
| HMI_NMR_EKI | HMI input |
| NMR_EKI | Send command (bit) to NMR |
| HMI_NMR_ET | HMI input |
| NMR_ET | Send command (bit) to NMR |
| HMI_NMR_EKP | HMI input |
| NMR_EKP | Send command (bit) to NMR |
| HMI_NMR_EM | HMI input |
| NMR_EM | Send command (bit) to NMR |
| HMI_NMR_EX | HMI input |
| NMR_EX | Send command (bit) to NMR |
| HMI_NMR_EH | HMI input |
| NMR_EH | Send command (bit) to NMR |
| HMI_NMR_EB_test | HMI input |
| NMR_EB_test | Send command (bit) to NMR |

| Variable | Description |
| --- | --- |
| MVI94ASCII | Types ASCII |
| New_Data | Control bit |
| NMR_On | Alias for Dipole:4:O.Data.10 |
| PSU_timer | Timer: checks for MPS comm. Error |
| PSU_comm_error | Bit indicating communication error |
| NMR_timer | Timer: checks for NMR comm. Error |
| NMR_comm_error | Bit indicating communication error |
| Read_data_input | Buffers readback from the NMR & MPS |
| Read_data_output | NMR(MPS) readback minus the carriage return(if any) |
| CR | String “carriagereturn” $r |
| Count | Range:0-22 |
| MPS_Status_Read | Reads back the MPS status |
| NMR_GetStatus | Bit that controls the commands going out to the NMR |
| NMR_EB_cmd_sent | EBS command sent bit |
| NMR_EBSC_read | Readback of the EBS |
| NMR_cmd_Read | Readback of any NMR command sent out in SString[2] |
| NMR_Enq_CH1 | The first digit of the NMR display. |
| NMR_Enq_Read | Reads the field of the magnet |
| MPS_cmd_Read | Readback of any MPS command sent out in SString[13] |
| PSU_Error_Number |  |
| MPS_cmd_tim | Waits for 20msecs for error number from MPS, if no response then next command is sent. |
| Pcount | If not incrementing the PSU is not responding |
| Scount | If not incrementing the NMR is not responding |
| MPS_cmd_state_Read | Reads the command state of the MPS whether, REMOTE, LOCAL or LOCK |
| PSU_Output_current | Output current(response to AD 0$r) |
| PSU_Output_voltage | Output voltage(response to AD 2$r) |
| MPS_ADC_value | MPS ADC readback value |
| Set_value_MPS | MPS set value readback |
| MPS_Slew_value | Slew rate of MPS |
| NMR_Status | Converted NMR Status from ASCII(hex) to decimal. Result = (SINT[1] * 16) + (SINT[2]) |
| NMR_Status[4] | Converted NMR Status from ASCII(hex) to decimal. Result = (SINT[0] * 4096 + (SINT[1] * 256) + (SINT[2] * 16) + SINT[3]) |
| Char_Cnt_OverFlow | Latches if data to be written to NMR is greater than 10. |
| Timer | Time in between the commands being sent to NMR |
| NMR_NULL_test | Moves a null string to SString[2](NMR command) and SString[13](MPS command), after the commands have been sent to the NMR & MPS resp. |
| WriteLength_hold | Number of characters, when write string length is greater than 10. |
| char_hold | Integer part of [WriteLength_hold / 10] |
| Xmit_length | The number of characters that are processed in this scan |
| Xmit Xmit.ACC | Counter Number of characters that are processed each scan (b/n 1-9). |
| BlockID_OnTX | Helps to write new data only to the port |
| NMR_commands_Subroutine |  |
| Variable | Description |
| NMR_ER0 | Command “ER0” |
| NMR_LR_cmd | Local/Remote command |
| NMR_EB_cmd | Command “EB” |
| NMR_EB_man_cmd | Manual command “EB” |
| NMR_Rst_cmd | Command “RS” |
| NMR_ER1_cmd | Command “ER1” |
| NMR_ECL_cmd | Command “ECL” |
| NMR_ECH_cmd | Command “ECH” |
| NMR_ECS_cmd | Command “ECS” |
| NMR_StartSearch | Command”H$r$l” |
| NMR_QuitSearch | Command”Q” |
| NMR_Rem | Command”R” |
| NMR_Loc | Command local “L” |
| NMR_DisT | Command display “T” tesla |
| NMR_A1 | Command “A1” |
| NMR_A0 | Command “A0” |
| NMR_POP | Command ”F1” polarity positive |
| NMR_PON | Command ”F0” polarity negative |
| NMR_sear_speed | Command “O” |
| NMR_Mux_cmd | Command ”P” |
| NMR_Mux_range_cmd | Command ”X” |
| ES_settling_time | Command ”ES” |
| NMR_EKI_cmd | Command ”EKI” |
| NMR_EKP_cmd | Command ”EKP” |
| NMR_ET_cmd | Command ”ET” |
| NMR_EM_cmd | Command ”EM” |
| NMR_EX_cmd | Command ”EX” |
| NMR_EH_cmd | Command ”EH” |
| NMR_EFC_cmd | EFC,WA $14999999$14$r$l |
| NMR_EBSC_cmd | EBS,C$r$l |
| MPS_Wa_cmd | Writes a value b/n 0 to 999999 to the regulation module to set output current. It uses a leading zero format. |
| MPS_Wa_zero_cmd | Sets output current to zero |
| MPS_Slew_write_cmd | Writes DAC 1 absolute |
| MPS_PowerN | Switches on the main contact of the power supply |
| MPS_PowerF | Switches off the main contact of the power supply |
| MPS_RS | Clears non pending interlocks |
| MPS_PONeg | Changes polarity to negative |
| MPS_POPos | Changes polarity to positive |
| MPS_Remote | Switches PS to remote operation |
| MPS_GlobalF | Switches on auxiliary output port(similar to N1) |
| MPS_SlowF | Switches off the PS and sets the set value to zero |
| MPS_Unlock | Releases the local LOCK state |
| MPS_Loc_cmd | Switches PS to local operation |

- Interlock

9.1 Variable tag information

| Variable | Description |
| --- | --- |
| Quench_max | 2800 mV |
| Quench_min | -2800 mV |
| DV_max | 150mV |
| DV_min | -150mV |
| Delay_SQD | 3 secs |
| No_Interlocks | No interlocks |
| Reset_Interlock | HMI command to reset interlocks |
| Sfw_QD_first | Indicates software QD is the first interlock |
| Sfw_QD_interlock | Software QD indicates voltages out of range |
| R_int_HMI | HMI input: Reset interlock Dipole:4:O.Data.13 Dipole:4:O.Data.14 Dipole:4:O.Data.15 |
| QD_U1 | Alias of Dipole:1:I.Data.0 |
| QD_L1 | Alias of Dipole:1:I.Data.1 |
| QD_CL_L_first | Quench Detector Current lead left interlock |
| QD_U2 | Alias of Dipole:1:I.Data.2 |
| QD_MCoil_Left_first | Quench detector magnetic coil left interlock |
| QD_L2 | Alias of Dipole:1:I.Data.3 |
| QD_MCoil_Right_first | Quench detector magnetic coil right interlock |
| QD_U3 | Alias of Dipole:1:I.Data.4 |
| QD_L3 | Alias of Dipole:1:I.Data.5 |
| QD_CH3_Spare_first | Quench detector Channel 3 spare interlock |
| QD_U4 | Alias of Dipole:1:I.Data.6 |
| QD_L4 | Alias of Dipole:1:I.Data.7 |
| QD_CL_R_first | Quench Detector Current lead right interlock |
| Hw_QD_interlock | Hardware QD interlock: sum of all QD interlocks |
| H_LHe_Interlock | Helium liquid level is outside its limits |
| h_LHe_first_interlock | Indicates that this is the first interlock |
| T_mag_IntMax | 5.2 K : Set point for magnet temperature interlock |
| T_LHe_1_fault to T_LHe_4_fault | Aliases for Channel faults Dipole: 5:I. Ch8Fault to Dipole: 5:I. Ch11Fault |
| T_LHe_L_CL_error | Carbon glass LHe left current lead error |
| T_LHe_R_CL_error | Carbon glass LHe left current lead error |
| T_LHe_R_CL_C_Fault | Alias for Channel fault Dipole: 5:I. Ch15Fault |
| T_LHe_L_CL_C_Fault | Alias for Channel fault Dipole: 5:I. Ch14Fault |
| T_CL_error | Current leads error |
| T_mag_interlock | Helium magnet temperature interlock |
| T_mag_first_interlock | Indicates Helium magnet temperature is the first interlock |
| T_LHe_R | Calculated value of Carbon glass right current lead |
| CL_max_temp | Current lead max temperature |
| T_LHe_L | Calculated value of Carbon glass right current lead |
| T_CL_interlock | Indicates current leads are greater than maximum and there are channel faults |
| T_CL_first_interlock | Indicates CL are the first interlocks |
| m_flow_R_fault m_flow_L_fault | Dipole: 6:I. Ch1Fault Dipole: 6:I. Ch0Fault |
| M_flow_interlock | Mass flow level interlock |
| M_flow_first_interlock | Indicates flow level is the first interlock |
| F_int_max | Maximum limit |
| F_R1_Fault F_L1_Fault F_R2_Fault F_L2_Fault F_R3_Fault F_L3_Fault F_R4_Fault F_L4_Fault | Dipole:8:I.Ch8Fault Dipole:8:I.Ch9Fault Dipole:8:I.Ch10Fault Dipole:8:I.Ch11Fault Dipole:8:I.Ch12Fault Dipole:8:I.Ch13Fault Dipole:8:I.Ch14Fault Dipole:8:I.Ch15Fault |
| Force_interlock | Indicates if forces are higher than the max and if there are channel faults. |
| Force_first_interlock | Indicates force is the first interlock |
| HMI_Fast_discharge | HMI input: to ramp down the magnet fast by energy dump |
| HMI_slow_discharge | HMI input: to ramp down the magnet slowly by power supply |
| PLC_fast_discharge | User fast discharge from HMI |
| PLC_slow_discharge | User slow discharge from HMI |
| HMI_fast_discharge_first | Indicates this is the first interlock |
| HMI_slow_discharge_first | Indicates this is the first interlock |
| p_He_first_interlock | Indicates pHe is over its limits and that this is the first interlock |
| p_N2_first_interlock | Indicates pN2 is over its limits and that this is the first interlock |
| Thermovac_max | 794.3 torr |
| Thermovac_min | .001259 torr |
| Thermovac_interlock | Indicates thermovac is over its limits |
| Thermovac_first_interlock | Indicates its the first interlock |
| Penning_max | .00794 torr |
| Penning_min | 1.259* 10 –9 torr |
| Penning_interlock | Indicates penningvac is over its limits |
| Penning_first_interlock | Indicates it’s the first interlock |
| He_Temp_delay | 60 secs |
| dTBobbin_interlock | He error |
| dTBobb_first_interlock | Indicates it’s the first interlock |
| p_Vac_min | .001 mbar |
| Vac_delay | 60 secs |
| p_vac_interlock | Indicates that vacuum pressure is greater than its minimum for 60 secs |
| p_vac_first_interlock | Indicates it’s the first interlock |
| PSU_Sum_Interlock | Alias of MPS_Status_Read.DATA[9].0 |
| PSU_Sum_first_Interlock | Indicates it’s the first interlock |

10	Voltage Sensors

The voltages across the super conducting dipole coils as well as the vapor cooled current leads are detected with voltage taps on the superconductor and on both ends of each current lead. For the transmission of the voltage signal inside the cryostat and the reservoir two types of wires are used.

The voltage sense wires from the super conducting dipole coils in the cryostat to the helium reservoir are made of AWG-28 polyimid insulated wires from HABIA CABLE AB. From the soldering lug strip inside the helium reservoir to the sockets on the top of the reservoir, the voltage sense wires are AWG-24 (FEP) insulated wires from the same manufacturer.

Both, the AEG-28 and AWG-34 voltage sense wires, are surrounded from a flexible silicone-glass-fabric tube to withstand a radiation dose of 106 Gy. All voltage taps are protected by a series 100 KOhm resistors to prevent voltage tap failure in the event of a fault to ground.

| Type | HT 2807 TF (AWG 28) |
| --- | --- |
| Conductor | Silver plated copper |
| Strands | 7 X 0.13 mm |
| Diameter | 0.38mm |
| Area | 0.089 mm2 |
| DC-Resistance at 300K | 234 /km |
| Voltage rating | 300 V RMS |
| Test voltage | 3000 V RMS |
| Insulated Wire: |  |
| Min. Diameter | 0.55 mm |
| Max Diameter | 0.63 mm |
| Weight | 1.1 Kg/km |

Table 10.1: Characteristics of the AWG-38 voltage sense wire

| Type | M-KT 2419 (AWG 24) |
| --- | --- |
| Conductor | Silver plated copper |
| Strands | 19 X 0.13 mm |
| Diameter | 0.64 mm |
| Area | 0.24 mm2 |
| DC-Resistance at 300 K | 77.5 /km |
| Voltage rating | 250 V RMS |
| Test Voltage | 2500 V RMS |
| Insulated Wire: |  |
| Min. Diameter | 0.86 mm |
| Max. Diameter | 0.96 mm |
| Weight | 3.2 kg/km |

Table 10.2: Characteristics of the AWG-24 voltage sense wire

10.1	 Location of Voltage Sensors

Voltage taps are located on both ends of each vapor cooled current lead and on both sides of each pancake coil of the dipole. Additional for the quench detection, three voltage taps are mounted symmetrical on the dipole coil. The voltage taps V1a (V1b) to V16a (V16b) are placed at the following locations:

V1a (b): Voltage tap on the warm end of the current lead, which is connected with the pancake #1 of the left coil

V2a (b): Voltage tap on the cold end of the current lead, which is connected with the pancake #1 of the left coil

V3a (b): Voltage tap at the begin of the left coil pancake #1

V4a (b): Voltage tap at the end of the left coil pancake #1

V5a (b): Voltage tap at the begin of the left coil pancake #2

V6a (b): Voltage tap at the end of the left coil pancake #2

V7a (b): Voltage tap at the begin of the left coil pancake #3

V8a (b): Voltage tap at the end of the left coil pancake #3

V9a (b): Voltage tap at the begin of the right coil pancake #4

V10a (b): Voltage tap at the end of the right coil pancake #4

V11a (b): Voltage tap at the begin of the right coil pancake #5

V12a (b): Voltage tap at the end of the right coil pancake #5

V13a (b): Voltage tap at the begin of the right coil pancake #6

V14a (b): Voltage tap at the end of the right coil pancake #6

V15a (b): Voltage tap on the cold end of the current lead that is connected with the pancake #6 of the left coil

V16a (b): Voltage tap on the warm end of the current lead that is connected with the pancake #6 of the left coil

The voltage taps VL, VM and VR are used for the quench detection of the HMS dipole. They are placed at the following locations:

VL: Voltage tap at the begin of the left coil pancake # 1

VM: Voltage tap between the left pancake coil # 3 and the right pancake coil # 4

VR: Voltage tap at the end of the right coil pancake # 6

10.2	Method of the Voltage tap measurement

The signal from the voltage taps goes into a signal conditioner SCM5B31-09D, which is then tapped into a 1756 IF-16 in Differential mode Voltage. In this task Voltages are monitored to check for errors generated by out of range values.4-20 mA signals from the Voltage Tap Transmitters are converted to read voltages on the front end. The output from the signal conditioner is 4 to 20 mA.

Current Leads:

4 mA     +500mV           Resolution: 1000/16 mV/mA

20 mA     -500mV

Pancake Coil:

4 mA       +32.7V            Resolution: 75.4/16 V/mA

20 mA      -32.7V

The signal from the voltage taps goes into a signal conditioner SCM5B31-09D, which is then tapped into a 1756 IF-16 in Differential mode Voltage.

Front end calibration:

U1_x to U8_x: Dipole:9:I.Ch0Data and Dipole:9:I.Ch7Data

Input range: -10v to 10V

Calibration: -10 to 10 is -10000 to 10000

The calibrated front end voltage is then calculated with the offset

| Voltage | Offset |
| --- | --- |
| U1 | 6.25629444e-4 |
| U2 | 3.12814722e-4 |
| U3 | 6.25629444e-4 |
| U4 | 6.25629444e-4 |
| U5 | 3.12814722e-4 |
| U6 | 3.12814722e-4 |
| U7 | 3.12814722e-4 |
| U8 | 3.12814722e-4 |

10.3	Variable tag information

| Variable | Description |
| --- | --- |
| U1_x to U8_x | Dipole: 9:I. Ch0Data to Dipole: 9:I. Ch7Data |
| U_min | -2800 mV |
| U_max | 2800 mV |
| U_lead_min | -150mV |
| U_lead_max | 150mV |
| U1_error to U8_error | Warning output |
| U_error | Summary of warnings |
| U2 to U7 | Differential voltages of the double pancakes from the coil. |
| U1 and U8 | Voltages from the current leads. |
| U1_error | (U1>U_lead_max) or (U2_lead_min) |
| U2_error | (U2>U_max) or (U2<U_min) |

Table 10.3: Variable tags and description

11	EPICS variables

| PLC | Description |
| --- | --- |
| CEV6711C | 4K Flow Limit |
| CEV6711C_ORBV | 4K Supply Valve Position |
| CEV6721C_ORBV | 4K Return Valve Position |
| CEV6731C_ORBV | 15 K Supply Valve Position |
| CEV6741C_ORBV | 20 K Return Valve Position |
| CEV6751C_ORBV | LN2 Supply Valve Position |
| CEV6781C_ORBV | 4 K to 20 K Return Cross Over Valve Position |
| CFI6010 | Warm He Supply Flow |
| CFI6030 | Lead Return Flow all Halls |
| CFI60DLP | Warm He Return Flow |
| CFI6711A | Hall A 4K Supply Flow |
| CFI6711B | Hall B 4K Supply Flow |
| CFI6711C | Hall C 4K Supply Flow |
| CFI6731C | 15 K Supply Flow |
| CFI6751C | LN2 Supply Flow |
| CLL671SC | 4.5 K Buffer Level |
| CLL675SC | LN2 Buffer Level |
| CPI6010 | Warm He Supply Pressure |
| CPI6030 | Lead Return Pressure all Halls |
| CPI603QC | Quench Line Pressure |
| CPI60DLP | Warm He Return Pressure |
| CPI671SC | 4K Supply Pressure ESR |
| CPI671T | 4K Supply Pressure |
| CPI672 | 4.5 K Return Pressure all Halls |
| CPI673 | 15 K Supply Pressure |
| CPI674 | 20 K Return Pressure |
| CPI6751 | LN2 Supply Pressure |
| CPI9521 | 4K Return Pressure |
| CTD671SC | 4K Supply Temperature |
| CTD672 | 4.5 K Return Temperature all Halls |
| CTD673 | 15 K Supply Temperature all Halls |
| CTD674 | 20 K Return Temperature |
| CTD9521 | 4K Return Temperature |
| CTP6751 | LN2 Supply Temperature |
| T_TL_1 | Transfer Line Supply Temperature |
| T_TL_2 | Transfer Line Return Temperature |
| T_TL_3 | Transfer Line LN2 Temperature |
| T_TL_4 | Transfer Line Dipole Return Temperature |
| T_TL_5 | Transfer Line Dipole Supply Temperature |
| T_TL_6 | Transfer Line Q1 Warm Return Temperature |
| T_TL_7 | Transfer Line Q2 Warm Return Temperature |
| T_TL_8 | Transfer Line Q3 Warm Return Temperature |