## Sheet1
Hall C - PLC Task List issued on May 01, 2018
Item | Description | Person | Duration (days)
1 | Interactive HMI data logging upgrade installation and operation | TBD | 20
2 | End of life for Windows 7 upgrade to Windows 10 | TBD | 10
3 | Develop “on loop” current regulation routine | Tyler | 10
4 | Add HMS “spectrometer vacuum” controls | Tyler | 2
5 | Modify SHMS shutter not installed status | Amanda | 1
6 | Connect to system and program UPS status | Tyler | 2
7 | Tune valve PID | Brian | 5
8 | Rewire and program SHMS LVDT I/O modules to single ended | Pablo | 4
9 | Program PLC communication with new NMR units | Pablo, Tyler, Peter | 5
10 | Add HMS Quadrupole hall probe readouts to PLC | Brian | 3
11 | Add HMS Shutter controls and status | Amanda | 1
12 | Add spectrometer rotation electric break control | Brian | 5
13 | Remote alarm notification to on-call support staff | Amanda | 4
14 | Re-program for replacement SHMS LHe/LN2 meters | Amanda | 15
15 | HMS & SHMS Dipole field regulation routine | Pablo | 10
Hall C - PLC Task List issued on June 05, 2018
Item | Description | Priority | Person | Duration (days) | Status
1 | HMS & SHMS Dipole field regulation routine | 1 | TBD | ?
2 | PLC- Test Ethernet vs Controlnet interface. | 1 | TBD | ?
3 | PLC - New NMR communication to PSU through PLC | 1 | Pablo, Tyler, Brian, Peter | 5 | In Progress
4 | Add spectrometer rotation electric break control
5 | PLC - Add HMS Spectrometer Vacuum to controls | 2 | Tyler | 2 | In Progress
6 | PLC - Data Logging upgrade, install and make operational | 2 | TBD | 20
7 | PLC - develop "on loop" current regulation routine for quad's PSU. | 2 | Tyler | 10
8 | PLC - Tune valve responses | 2 | Brian | 5
9 | PLC - wire UPS status to controls | 2 | Tyler | 2 | In Progress
10 | PLC - modify SHMS shutter not in place status | 2 | Amanda | 1 | In Progress
11 | PLC - Alarm notification to on-call staff | 3 | Amanda | 4
12 | PLC - Add HMS quadrupoles hall probe readouts to PLC | 3 | Brian | 3
13 | PLC - Add HMS shutter controls and status | 3 | Amanda | 1 | In Progress
14 | PLC - Change SHMS LVDT I/O module from Differential to Single ended | 3 | Amanda | 4
15 | PLC - End of life for Windows 7 upgrade to windows 10 (next year?) | 4 | TBD | 10
Comments:
Tasks highlighted in yellow were added in the new list generated on 06/05/2018
Tasks highlighted in orange were removed in the new list generated on 06/05/2018
Tasks highlighted in green are in progress

## dsg
Update Date: 01/30/2019
Hall C - PLC Tasks List
Item | Description | Priority | Primary Person | Start Date | Status | Comments | Suggested Duration (days) by Hall C
1 | HMS & SHMS Dipole field regulation routine | 1 | Pablo | 2018-06-14 | Completed | Completed on 09/13/2018. Being checked by Mike Fowler | 10
2 | New NMR communication through PLC to PSU | 1 | Brian | 2018-05-10 | Does not work as expected | Adding code in SBC card to handle "Locking" NMR conditions. Issues to lock PT2026 when filed > 1.4 T. PT2026 needs different RF Pulse settings (under advanced) when HMS dipole is at 1.8 T compared to when it’s at 1.4 T. | 5
3 | Test Ethernet vs Controlnet interface. | 1 | Pablo | 2018-06-07 | Completed | Completed on 06/13/ 2018 | N/A
4 | Swapping of Controlnet by Ethernet modules in SHMS | 1 | Pablo Brian | 2018-07-03 | Completed | Completed on 7/13/2018 | N/A
5 | Add spectrometer rotation electric break control | 2 | Hall C | N/A | Completed | Completed on 08/03/2018 | 5
6 | Add HMS Spectrometer Vacuum to controls | 2 | Tyler | 2018-05-29 | Completed | Completed on 07/23/2018. To be downloaded to PLC by Steve or Mike. | 2
7 | Data Logging upgrade, install and make operational | 2 | Pablo | 2018-07-12 | On hold | Denied access by Hall C; unable to access SHMS and HMS HMI screens | 20
8 | Develop "on loop" current regulation routine for quads' (3) PSU. | 2 | Amanda | 2018-06-14 | Completed | Completed on 08/06/2018. Routine implemented and running in HMS PLC. | 10
9 | Tune valve responses | 2 | Amanda | - | Not started | Awaiting information on the task itself. | 5
10 | Wire UPS status to controls | 2 | Tyler | 2018-05-30 | Completed | PLC program completed, information about the connections, wiring and drawings required was completed on 09/13/2018 | 2
11 | Modify SHMS shutter not in place status | 2 | Hall C | N/A | Completed | Completed on 08/03/2018 | 1
12 | Add HMS shutter controls and status | 3 | Hall C | N/A | Completed | Completed on 08/03/2018 | 1
13 | Alarm notification to on-call staff | 3 | TBD | - | Being developed as a new EPICS taks request | Should be done in EPICS | 4
14 | Add HMS quadrupoles hall probe readouts to PLC | 3 | Hall C | N/A | Completed | Completed on 08/29/ 2018 | 3
Th | Change SHMS LVDT I/O module from Differential to Single ended | 3 | Amanda | - | Not started | Awaiting information about available hardware and PLC module channels to be modified. | 4
16 | End of life for Windows 7 upgrade to windows 10 (next year?) | 4 | Pablo | 2018-07-12 | Completed | Completed on 10/02/2018. No compatibility issues found | 10
17 | Upgrade SHMS PLC from version 16 to version 20 | 1 | Pablo Brian Amanda Tyler | 2018-07-03 | Completed | Completed on 7/13/2018 | N/A
18 | Upgrade HMS PLC from version 16 to version 20 | N/A | Brian Tyler Amanda | 2018-07-19 | Completed | Completed on 01/18/2019 | N/A