## Sheet1
Date: | 2019-04-15
By: | Pablo Campero
HMS
No | PLC Tag Name | Suggested EPICS PV Name | Data Type | Client Access | Description
1 | HMS_PLC_HEARTBEAT | ecHMS_PLC_HEARTBEAT | Boolean | Read | PLC heartbeat pulse signal
2 | HMS_PLC_HEARTBEAT_COUNTER | ecHMS_PLC_HEARTBEAT_COUNTER | DINT | Read | PLC counter value
3 | HMS_PLC_COMM_FAILED | ecHMS_PLC_COMM_FAILED | Boolean | Read | PLC communication status: 0 = Ok & 1 = Failed
4 | HMS_IOC_HERTBEAT | ecHMS_IOC_HEARTBEAT | Boolean | Read/Write | IOC heartbeat pulse signal
5 | HMS_IOC_HEARTBEAT_COUNTER | ecHMS_IOC_HEARTBEAT_COUNTER | DINT | Read/Write | IOC Counter value from EPICS
6 | HMS_IOC_COMM_FAILED | ecHMS_IOC_COMM_FAILED | Boolean | Read | IOC communication status: 0 = Ok & 1 = Failed
7 | HMS_RESET_COMMS | ecHMS_RESET_COMMS | Boolean | Read/Write | Button to reset communications failed status
8 | HMS_PLC_EPICS_COMMS_STAT | ecHMS_PLC_EPICS_COMMS_STAT | Boolean | Read | Overall communication status between EPICS and PLC
SHMS
No | PLC Tag Name | Suggested EPICS PV Name | Data Type | Client Access | Description
1 | SHMS_PLC_HEARTBEAT | ecSHMS_PLC_HEARTBEAT | Boolean | Read | PLC heartbeat pulse signal
2 | SHMS_PLC_HEARTBEAT_COUNTER | ecSHMS_PLC_HEARTBEAT_COUNTER | DINT | Read | PLC counter value
3 | SHMS_PLC_COMM_FAILED | ecSHMS_PLC_COMM_FAILED | Boolean | Read | PLC communication status: 0 = Ok & 1 = Failed
4 | SHMS_IOC_HERTBEAT | ecSHMS_IOC_HEARTBEAT | Boolean | Read/Write | IOC heartbeat pulse signal
5 | SHMS_IOC_HEARTBEAT_COUNTER | ecSHMS_IOC_HEARTBEAT_COUNTER | DINT | Read/Write | Counter value from EPICS
6 | SHMS_IOC_COMM_FAILED | ecSHMS_IOC_COMM_FAILED | Boolean | Read | IOC communication status: 0 = Ok & 1 = Failed
7 | SHMS_RESET_COMMS | ecSHMS_RESET_COMMS | Boolean | Read/Write | Button to reset communications failed status
8 | SHMS_PLC_EPICS_COMMS_STAT | ecSHMS_PLC_EPICS_COMMS_STAT | Boolean | Read | Overall communication status between EPICS and PLC
Note: For the addition of the above SHMS/HMS PLC tags in OPC Server (KepServerEX 6.5); consider the creation of a new Tag Group named: "HEARTBEAT". Add one Tag Group per each SHMS and HMS PLC respectively. This is required in order to match the fields for IN/OUT address configured in the database file running by st.cmd on OpcIocShell software