|  |  | TITLE: | ES&H Manual |
| --- | --- | --- | --- |
| DOCUMENT ID: | 6540 Appendix T1 Oxygen Deficiency Hazard (ODH) Safety Review |  |  |

DRAFT

Jefferson Lab has determined that working within an ODH area carries an unmitigated Risk Code >2. At a minimum an ODH Safety Review is required prior to the introduction of an ODH into an area, and all tasks assigned are discussed with the supervisor prior to commencement of work. An Operational Safety Procedure (OSP) is required when work is considered to be a Risk Code >2 in accordance with ES&H Manual Chapter 3210 Work Planning, Control, and Authorization Process.

The purpose of an Oxygen Deficiency Hazard (ODH) Safety Review is to enable Jefferson Lab to determine the level of rigor to be applied when an ODH source is introduced to, or recognized to be in, an area.  This appendix provides instructions on how to complete an ODH Safety Review Form (Link to be established upon approval of document) so an accurate determination of risk can be made and appropriate precautions can be implemented.

- Scope

This form is to be filled out for an area before an ODH is introduced, or when it is recognized, (including, but not limited to: fixed source, and permanently installed equipment).  This form is also used to assist in identifying areas that have the potential to become an ODH.

The process steps for this procedure are performed in coordination with ES&H Manual Chapter 6540 Oxygen Deficiency Hazard Control Program (Link to be established upon approval of document.)

- Responsibilities

  - Anyone at Jefferson Lab

- Complete the ODH Safety Review Form (Link to be established upon approval of document prior to introducing, or alerting ODHs, or as requested for your work area.

  - ODH Safety

- Review and, if acceptable, approve ODH Safety Review document(s).  (Recommend a more rigorous review as appropriate, up to and including an ODH Risk Assessment or Facility Design Review.)

- Designate the appropriate ODH classification for an area.

- Verify ODH equipment safeguards, inventory requirements, posting, and labeling, are in-place prior to introduction of the ODH.

- When to Perform

An ODH Safety Review is performed when gas is proposed, altered, discovered, or as requested in accordance with ES&H Manual Chapter 3210 Work Planning, Control, and Authorization Process.  Relevant factors include, but are not limited to:

- Volume of the area.

- Potential volume of the gas.

- Work to be performed in the area.

- Engineering controls currently in place.

- Required administrative controls.

- ODH Safety Review		 (Link to be established upon approval of document)

  - Part 1 – Preliminary Analysis: Using the ODH Safety Review Form, fill in all information requested.

- Introduction

- Task Title:  Brief description of work.

- Task Number: As applicable per department procedures.

- Location, Specify building, room, or area.

- Effective Date: Date which the ODH will be introduced (not necessarily the date the form is approved).

- Expiration Date:  Date by which the area must be re-assessed or hazard will no longer apply (not to exceed three years).

- Author/Lead Worker/Division/Department:  Print name of person responsible for the ODH their division/department.

- Preliminary Information

- Gas(es) to be Introduced:  List the name and concentration of the gas(es).  Denote any additional hazard issues that may be of concern.

- Denote Hazard Category (See ES&H Manual Chapter 6150 Compressed Gases)

- Room Floor Plan

Attach a Room Floor Plan denoting the location of the ODH.  (See Facilities Management and Logistics “List of Facilities - Floor Plan Highlighted by Room Standard” for square footage.)

- Preliminary ODH Calculation

Depending on the location of your source, complete the appropriate column:

| IF | THEN |  |
| --- | --- | --- |
| Source is located inside the proposed ODH area | Calculate: | 21(VR – VG) VR |
| OR |  |  |
| Source is located OUTSIDE the proposed ODH area | Calculate: | 21(VR – Q) * VR |
| Where: VR = the total volume of the room (ft3) VG = the volume of gas at room temperature and pressure Q = Volumetric flow rate of gas into room at room temperature and pressure (Contact Engineering if you require assistance) * Assuming one fresh air change per hour (ACH). If more than one ACH is needed additional review may be required. |  |  |

| If Resulting % Oxygen is: | Then |
| --- | --- |
| >19.5 | Submit the form to ODH Safety. (See Section 4.3 Submittal below.) |
| <19.5 | Continue to 5.2 Part Two – Additional Details |

  - Part Two – Additional Details

- Include:

- Engineering Controls:  List those that are already in place and those that are planned.  (Attach additional sheets as necessary)

- Administrative Controls:  List those that are already in place, or are required before work.  Including, but not limited to:

- Training Required

- Standard Protecting Measures

- Work Control Documents

- Attachments:  List all attachments; include e-mail confirmations, document numbers, etc. so that your calculations can be verified.

  - Submittal

- Author/Lead Worker – Submit the completed form to ODH Safety for ODH designation and approval.

- ODH Safety – review the completed form:

        - Perform a walk-through to verify all labeling, posting, engineering and administrative safeguards, equipment and inventory requirements are in-place.

        - If Acceptable (>19.5):

    - Denote ODH designation, designate approval, and return the form to Author/Lead Worker,

OR

  - If Unacceptable (<19.5 or other concern is found)

      - Arrange for an ODH Risk Assessment.

      - Return the form to Author/Lead Worker, for additional information.

- Author/Lead Worker:

- Ensures required mitigation measures are installed/in-place (re-submits form for ODH Safety approval if necessary).

- Obtains additional review and final approval signatures per department procedures.

  - Distribution:

Upon final approval the Author/Lead Worker makes the following distributions:

- Original: to be appropriately posted in accordance with department procedures.

- Copies to: affected area and ESH&Q Document Control.

- ODH Safety Review Flowchart

- Revision Summary

Revision 1 – Updated to reflect current laboratory operations.

|  | ISSUING AUTHORITY | TECHNICAL POINT-OF-CONTACT | APPROVAL DATE | EFFECTIVE DATE | EXPIRATION DATE | REV. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ESH&Q Division | Dick Owen |  |  |  |  |  |  |

This document is controlled as an on line file.  It may be printed but the print copy is not a controlled document.  It is the user’s responsibility to ensure that the document is the same revision as the current on line file.  This copy was printed on 7/28/2026.