|  |  | TITLE: | ES&H Manual |
| --- | --- | --- | --- |
| DOCUMENT ID: | 6630 Appendix T2 Engineering Controls – Local and Portable Exhaust Systems |  |  |

- Purpose

Whenever respiratory hazards cannot feasibly be mitigated through material substitution, engineering controls (in the form of local and/or portable exhaust systems) are the next preferred methods.  This appendix provides how to determine if an engineering control is required; appropriate use parameters; and repair, maintenance, and inspection schedules.

- Scope

This appendix covers the local and portable exhaust systems available at Jefferson Lab.

The following table provides minimum capture velocities required to mitigate a hazard for a typical condition, and the contaminant velocity.  (These are representative conditions found at Jefferson Lab, other conditions may apply.  Contact Industrial Hygiene if there is a concern regarding your specific condition.)

Table 1:  Local/Portable Exhaust

| Condition Examples | Contaminant Velocity | Minimum Capture Velocity (feet per minute) |
| --- | --- | --- |
| Vapors from degreasing, or soldering | No significant velocity | 50–100 |
| Spray paint booths, welding, solvent, and acid work | Low initial velocity | 100–200 |
| Spray painting into shallow booths, container filling, and crushing | Significant velocity | 200–500 |
| Grinding, and abrasive-blasting | High velocity | 500–2000 |

- Responsibilities

NOTE:	Management authority may be delegated at the discretion of the responsible manager.

  - Anyone at Jefferson Lab

- Request an equipment/area hazard evaluation from Industrial Hygiene if you have concerns regarding air quality.

- Use exhaust systems in accordance with intended condition.

- Submit a Facilities Management Work Request when equipment is not performing up to standards.

  - Facilities Management

- Repair exhaust systems as requested and maintain per manufactures recommendations.

- Contact Industrial Hygiene when repair/maintenance activities have been performed.

  - Industrial Hygiene

- Recommend appropriate mitigation (including material substitution) for respiratory hazards in accordance with findings from the hazard evaluation.

- Perform and record exhaust system inspections.

- Process Steps

  - Determining Need

In accordance with your Task Hazard Analysis, request a hazard evaluation for the work condition.

Flow Chart:

Determine if Exhaust System is Required

| If | Then |
| --- | --- |
| Material Substitution | Substitute Material. Continue Work |
| Local Exhaust System Required* | Submit a Facilities Management Work Request. (This could include ES&H Manual Chapter 3110 Facilities Design Review) |
| Portable Exhaust System Required | Obtain system training. Continue work. |
| *All local exhaust units are installed by Facilities Management. |  |

  - Use of Exhaust System:

    - Prior to use:

- Read and abide by manufacturers instructions.

- Ensure air flow is adequate for the condition.

- Read the Inspection Label:

  - Ensure inspection is valid (within one year of previous inspection) (contact Industrial Hygiene if out of date.)

  - Set work up to abide by:

    - appropriate sash height

    - working capture distances

| Example Inspection Labels |  |  |
| --- | --- | --- |
| FUME HOOD SURVEY HOOD TYPE _______________ HOOD ID# __________________ BLDG# ____________________ ROOM# ____________________ DATE ____________________ RECOMMENDED HOOD HEIGHT: FACE VELOCITY = 80 FPM: _____” # FACE VELOCITY = 100 FPM: ____” FACE VELOCITY = 120 FPM: ____” TECHNICIAN: _____________ Chemical Fume Hood Inspection Label |  | # CAPTURE FUME HOOD SURVEY # HOOD ID# ____________________ # BLDG. # ______________________ # ROOM# ______________________ # DATE ________________________ ## Capture Velocity _______________ fpm Distance from hood opening _____ inches Technician: ______________________ Capture Hood Inspection Label |

    - During use:

Abide by the following controls:

| Parameter | Control |
| --- | --- |
| Face velocity | - Maintain appropriate sash height or working capture distances. - Maintain the hood sash at the smallest practicable open area. - Use the sash as a protective shield. |
| Cross drafts | Position material to minimize cross drafts. |
| Turbulence and/or Dead Spots | Minimize by: - Regulating face velocity - Placing items at least 6-inches from the opening. - Raising bulky objects off the work surface. |
| Capture velocity | 100% capture is required. |
| Storage | Hoods are not to be used for: - Routine storage or - Evaporation of spent chemicals. |
| Body Positioning | Keep head and body out of the pathway between contaminant/condition and capture. |
| Personal Protective Equipment | Dependant on condition. See ES&H Manual Chapter 6620 Personal Protective Equipment Program for more information. |

NOTE: If at any time your exhaust system is not functioning adequately: - Discontinue use. - Submit a Facilities Management Work Request for repair or maintenance. - After repairs have been made, contact Industrial Hygiene to ensure adequate air flow.

    - Inspection

Industrial Hygiene performs the following inspections on exhaust systems:

- Before initial start-up;

- Annually thereafter;

- After any adjustment, modification, or maintenance.

| If the Hood: | Then |
| --- | --- |
| Passes inspection | - An appropriate hood inspection label is provided. |
| Does not pass inspection | - The hood is placed out of service. - A Facilities Management Work Request is submitted. - Another inspection is scheduled after repair of unit. |

- Reference:

- Industrial Ventilation, A Manual of Recommended Practice – 26th edition

- Revision Summary

Revision 1 – ##/##/#### – Updated to reflect current laboratory operations.

|  | ISSUING AUTHORITY | TECHNICAL POINT-OF-CONTACT | APPROVAL DATE | EXPIRATION DATE | REV. |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | ESH&Q Division | Jennifer Williams |  |  | 1 |  |

This document is controlled as an on line file.  It may be printed but the print copy is not a controlled document.  It is the user’s responsibility to ensure that the document is the same revision as the current on line file.  This copy was printed on 7/31/2026.