|  |  | TITLE: | ES&H Manual |
| --- | --- | --- | --- |
| DOCUMENT ID: | 6540 Appendix T1 Oxygen Deficiency Hazard (ODH) Safety Review |  |  |

DRAFT

Jefferson Lab has determined that working within an ODH area carries an unmitigated Risk Code >2. At a minimum, an ODH Safety Review is required prior to the introduction of an ODH into an area, and all tasks assigned are discussed with the supervisor prior to commencement of work. An Operational Safety Procedure (OSP) is required when work is considered to be a Risk Code >2 in accordance with ES&H Manual Chapter 3210 Work Planning, Control, and Authorization Process.

An Oxygen Deficiency Hazard (ODH) Safety Review is performed when gas is proposed, altered, discovered, or as requested in accordance with ES&H Manual Chapter 3210 Work Planning, Control, and Authorization Process.  Relevant factors include, but are not limited to:

- Volume of the area.

- Potential volume of the gas.

- Work to be performed in the area.

- Engineering controls currently in place.

- Required administrative controls.

- Existing ODH sources or installations.

This appendix provides instructions on how to complete an ODH Safety Review Form (Link to be established upon approval of document) so an accurate determination of risk can be made and appropriate mitigation can be implemented.

- Scope

The ODH Safety Review Form is to be filled out for any area before an ODH is introduced, or when it is recognized, including, but not limited to: fixed source, and permanently installed equipment.  This form is also used to assist in identifying areas that have the potential to become an ODH.

The process steps for this procedure are performed in coordination with ES&H Manual Chapter 6540 Oxygen Deficiency Hazard Control Program (Link to be established upon approval of document.)

- Responsibilities

  - Anyone at Jefferson Lab

- Complete the ODH Safety Review Form (Link to be established upon approval of document prior to introducing, or altering ODHs, or as requested for your work area.

  - ODH Safety Reviewer

- Review and, if acceptable, approve ODH Safety Review document(s).

- Submit request for a Facility Design Review or ODH Risk Assessment as appropriate.

- Designate the appropriate ODH classification for an area.

- Verify ODH equipment safeguards, inventory requirements, posting, and labeling, are in-place prior to introduction of the ODH.

  - ODH Analysis Design Authority

- Conduct ODH Risk Assessments when requested.

- Qualifications include:

  - Demonstrated ability to analyze and mitigate oxygen deficiency hazards within laboratory user systems.

  - Maintain appropriate training SAF103 Oxygen Deficiency Hazard

  - Technical proficiencies and knowledge of

    - ODH evaluations, calculations, design/implementation of control measures,

    - common compressed and liquefied gases,  mixed gas properties,

    - ODH propagation calculations,

    - 29 CFR 1910.146 Permit Required Confined Spaces

    - Pressurized gas mechanical systems with their associated failure modes analysis.

  - One of the following:

    - Completion of an engineering or physics degree, requiring four or more years of full time study, plus a minimum of five years experience relating to the technical requirements listed above.

    - Professional Engineering registration, recognized by the local jurisdiction, plus experience in systems relating to ODH classification, mitigation, evaluation, and their properties.

    - Jefferson Lab’s Engineering Manager approval

- ODH Safety Review		 (Link to be established upon approval of document)

  - Part 1 – Preliminary Analysis: Using the ODH Safety Review Form, fill in all information requested.

- Introduction

- Task Title:  Brief description of work.

- Task Number: As applicable per department procedures.

- Location, Specify building, room, or area and contiguous areas and relative position within the building or larger area.

- Effective Date: Date which the ODH will be introduced (not necessarily the date the form is approved).

- Expiration Date:  Date by which the area must be re-assessed or hazard will no longer apply (not to exceed three years).

- Document Owner/Division/Department:  Print name of person responsible for the work, their division/department.

- Preliminary Information

- Gas(es) to be Introduced:  List the name and concentration of the gas(es).  Denote any additional hazard issues that may be of concern.

- Denote Hazard Category (See ES&H Manual Chapter 6150 Compressed Gases)

- Denote if gas is self-contained? (In a Dewar or similar?)

- Attach copies of any related “Oxygen Deficiency Hazard Risk Assessments” for the building and any additional supporting documents/calculations.

- Room Floor Plan

Attach a Room Floor Plan denoting the location of the ODH.  (See Facilities Management and Logistics “List of Facilities - Floor Plan Highlighted by Room Standard” for square footage.)

- Preliminary ODH Calculation

Depending on the location of your source, complete the appropriate column:

| IF | THEN |  |
| --- | --- | --- |
| Container is located inside the proposed ODH area | Calculate: | 21(VR – VG) VR |
| OR |  |  |
| Container is located OUTSIDE the proposed ODH area | Calculate: | 21(VR – Q) * VR |
| Where: VR = the total volume of the room in cubic feet VG = the volume of gas at room temperature and pressure in cubic feet Q = Volumetric flow rate of gas into room at room temperature and pressure in cubic feet per hour (Contact Engineering if you require assistance) * Assuming one fresh air change per hour (ACH). If more than one ACH is needed additional review may be required. |  |  |

| If Resulting % Oxygen is: | Then |
| --- | --- |
| <19.5 | Continue to 4.2 Part Two – Additional Details |
| >19.5 | Submit the form to ODH Safety Reviewer. (See Section 4.3 Submittal below.) |

  - Part Two – Additional Information

- Include:

- Engineering Controls:  List those that are:

  - Already in place (e.g. fume hoods, valves, critical orifices), and

  - Planned.  (Attach additional sheets as necessary)

- Administrative Controls: including but not limited to:

- Training,

- Standard Protecting Measures,

- Work Control Documents

- Attachments:  Provide all attachments; include e-mail confirmations, document numbers, etc. so that your data can be verified.

- Submittal - Go to 4.3 Submittal

  - Submittal

- Submit the completed form: performed by the Document Owner

- Submit form to ODH Safety Reviewer for ODH designation and approval.

- Review the completed form: performed by the ODH Safety Reviewer

        - Perform a walk-through to verify all labeling, posting, engineering and administrative safeguards, equipment and inventory requirements are in-place.

        - If Acceptable (>19.5):

    - Denote ODH designation, designate approval, and return the form to Document Owner,

OR

  - If Unacceptable (<19.5 or other concern is found)

      - Arrange for an ODH Risk Assessment.

NOTE: Completed ODH Risk Assessments shall be returned to ODH Safety Reviewer for appropriate filing and distribution.

- Mitigation Actions: performed by Document Owner

- Ensure required mitigation measures are installed/in-place (re-submit form to ODH Safety Reviewer for approval if necessary).

- Obtain additional review and final approval signatures per department procedures.

  - Distribution:

Upon final approval the Document Owner makes the following distributions:

- Original: to be appropriately posted in accordance with department procedures.

- Copies to: affected area and ESH&Q Document Control.

- ODH Safety Review Flowchart

- Revision Summary

Revision 1 – ##/##/## – Updated to reflect current laboratory operations.

|  | ISSUING AUTHORITY | TECHNICAL POINT-OF-CONTACT | APPROVAL DATE | EXPIRATION DATE | REV. |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | ESH&Q Division | Dick Owen |  |  |  |  |

This document is controlled as an on line file.  It may be printed but the print copy is not a controlled document.  It is the user’s responsibility to ensure that the document is the same revision as the current on line file.  This copy was printed on 7/31/2026.