## Issued
Acceptance Criteria and Associated Travelers
| Qualification Parameter | Acceptance Criteria | Traveler | Data Field
Individual Cavity
1 | Lock frequency of accelerating mode (f0) | f0 = 1496.600 ± 0.2 MHz | C100R-VTA-CAV-VTRF | LockFrequency
2 | Maximum accelerating gradient (Emax) | Emax ≥ 25 MV/m | C100R-VTA-CAV-VTRF | Final_EmaxMVm
An administrative limit of 27 MV/m is in place during the cavity test
3 | Intrinsic quality factor (Q0) measured at T = 2.07 K, Eacc = 20 ± 0.3 MV/m | Q0 ≥ 8×109 | C100R-VTA-CAV-VTRF | Final_QoAt20MVm
4 | Maximum radiation dose rate (DR) at Eacc= 20 ± 0.3 MV/m | DR ≤ 1 ×10-3 mR/h (field emission free up to Emax) | C100R-VTA-CAV-VTRF | Final_RadMax (or Final_FEFree)
An administrative limit of 1 R/h is in place during the cavity test
5 | External-Q of the field-probe antenna (QextFP) | QextFP = (0.8 - 1.8)×1012 | C100R-VTA-CAV-VTRF | Qextfp
6 | Loaded-Q of Higher Order Modes (QL,HOM) | QL,HOM > 3×1012 | C100R-VTA-CAV-VTRF | QextHOMa and QextHOMb
7 | External-Q of the fundamental power coupler (QextFPC) as measured in the RF Incoming Inspection | QextFPC = (1.02 - 3.84)×107 | C100R-CAV-RFIN | QextFPC
Cavity String Assembly
8 | Maximum Cavity String Leak Rate (LRCST) | LRCST ≤ 1.00 ×10-8 Torr*l/s | C100R-CLNRM-CST-LEAK | *Traveler will be revised to include a data field for the leak rate. Currently the leak rate is recorded in the uploaded files and a checkbox is used to indicate if the string passed the leak check.
Per JLAB-TN-22-060
Cryomodule Assembly
9 | Maximum Cryomodule insulation vacuum Leak Rate (LRCM) | LRCM ≤ 1.00 ×10-9 Torr*l/s | C100R-CMA-VV-ASSY | UploadStripChartFile17 *update traveler to include data field for leak rate. Currently the leak rate is recorded in the uploaded files.
Per 11141-S-0033
10 | Maximum Helium circuit Leak Rate (LRHC), including the 2K and 50K circuits | LRHC ≤ 1.00 ×10-9 Torr*l/s | C100R-CMA-VV-ASSY | UploadStripChartFile11 *update traveler to include data field for leak rate. Currently the leak rate is recorded in the uploaded files.
Per 11141-S-0033
Cryomodule Testing
11 | Tuned Cavity Final Frequency | f0 = 1497.000 ± 0.1 MHz | C100R-ACC-CM-COMM | C#FreqPi
12 | Minimum Usable accelerating gradient for an individual cavity (Eop) at which the following 3 conditions are met: | Eop ≥ 19.2 MV/m | C100R-ACC-CM-COMM | C#InstEmaxop
radiation level is below 100 mR/hr,
the cavity can run stably for one hour
in both single cavity and eight cavity operation
0.5 MV/m below the quench field.
13 | Minimum usable CW voltage produced by a cryomodule (EG) with cavities running at their usable gradients simultaneously in GDR/SEL mode for at least one hour. | EG ≥ 108 MV | C100R-ACC-CM-COMM | CMInstMaxEnergy
14 | Maximum heat load at 2.07 K produced by a cryomodule (PCM,TOT) | PCM,TOT < 300 W | C100R-ACC-CM-COMM | CMInstRFHeat
Includes RF and static heat loads and coupler losses
15 | Maximum RF heat load of an individual cavity (PCAV,RF) at 19.2 MV/m and 2.07 K | Maximum PCAV,RF ≤ 30 W | C100R-ACC-CM-COMM | C#InstRFHeat
Nominal PCAV,RF ≤ 29 W

## Old
Acceptance Criteria and Associated Travelers
| Qualification Parameter | Acceptance Criteria | Traveler | Data Field
Individual Cavity
1 | Lock frequency of accelerating mode (f0) | f0 = 1496.600 ± 0.2 MHz | C100R-VTA-CAV-VTRF | LockFrequency
2 | Maximum accelerating gradient (Emax) | Emax ≥ 25 MV/m | C100R-VTA-CAV-VTRF | Final_EmaxMVm
An administrative limit of 27 MV/m is in place during the cavity test
3 | Intrinsic quality factor (Q0) measured at T = 2.07 K, Eacc = 20 ± 0.3 MV/m | Q0 ≥ 8×109 | C100R-VTA-CAV-VTRF | Final_QoAt20MVm
4 | Maximum radiation dose rate (DR) at Eacc= 20 ± 0.3 MV/m | DR ≤ 1 ×10-3 mR/h (field emission free up to Emax) | C100R-VTA-CAV-VTRF | Final_RadMax (or Final_FEFree)
An administrative limit of 1 R/h is in place during the cavity test
5 | External-Q of the field-probe antenna (QextFP) | QextFP = (0.8 - 1.8)×1012 | C100R-VTA-CAV-VTRF | Qextfp
6 | Loaded-Q of Higher Order Modes (QL,HOM) | QL,HOM > 3×1012 | C100R-VTA-CAV-VTRF | QextHOMa and QextHOMb
7 | External-Q of the fundamental power coupler (QextFPC) as measured in the RF Incoming Inspection | QextFPC = (1.02 - 3.84)×107 | C100R-CAV-RFIN | QextFPC
Cavity String Assembly
8 | Maximum Cavity String Leak Rate (LRCST) | LRCST ≤ 1.00 ×10-8 Torr*l/s | C100R-CLNRM-CST-LEAK | *Traveler will be revised to include a data field for the leak rate. Currently the leak rate is recorded in the uploaded files and a checkbox is used to indicate if the string passed the leak check.
Per JLAB-TN-22-060
Cryomodule Assembly
9 | Maximum Cryomodule insulation vacuum Leak Rate (LRCM) | LRCM ≤ 1.00 ×10-9 Torr*l/s | C100R-CMA-VV-ASSY | UploadStripChartFile17 *update traveler to include data field for leak rate. Currently the leak rate is recorded in the uploaded files.
Per 11141-S-0033
10 | Maximum Helium circuit Leak Rate (LRHC), including the 2K and 50K circuits | LRHC ≤ 1.00 ×10-9 Torr*l/s | C100R-CMA-VV-ASSY | UploadStripChartFile11 *update traveler to include data field for leak rate. Currently the leak rate is recorded in the uploaded files.
Per 11141-S-0033
| Maximum leak rate of an individual waveguide spool assembly (LRWG) | LRWG ≤ 2.00 ×10-10 Torr*l/s | C100R-CMA-CM-ASSY | *update traveler to include data field for leak rate. Currently the leak rate is recorded in the uploaded files and a checkbox is used to indicate if the leak check passed.
Per 11141-S-0029
| Tuner Operation Range | Range = 1497 MHz ± 50 kHz | C100R-CMA-VV-ASSY | CAV#_Freq15
Cryomodule Testing
11 | Tuned Cavity Final Frequency | f0 = 1497.000 ± 0.1 MHz | C100R-ACC-CM-COMM | C#FreqPi
12 | Minimum Usable accelerating gradient for an individual cavity (Eop) at which the following 3 conditions are met: | Eop ≥ 19.2 MV/m | C100R-ACC-CM-COMM | C#InstEmaxop
radiation level is below 100 mR/hr,
the cavity can run stably for one hour
in both single cavity and eight cavity operation
0.5 MV/m below the quench field.
13 | Minimum usable CW voltage produced by a cryomodule (EG) with cavities running at their usable gradients simultaneously in GDR/SEL mode for at least one hour. | EG ≥ 108 MV | C100R-ACC-CM-COMM | CMInstMaxEnergy
14 | Maximum heat load at 2.07 K produced by a cryomodule (PCM,TOT) | PCM,TOT < 300 W | C100R-ACC-CM-COMM | CMInstRFHeat
Includes RF and static heat loads and coupler losses
15 | Maximum RF heat load of an individual cavity (PCAV,RF) at 19.2 MV/m and 2.07 K | Maximum PCAV,RF ≤ 30 W | C100R-ACC-CM-COMM | C#InstRFHeat
Nominal PCAV,RF ≤ 29 W
| Beamline pressure at 2.07 K temperature (PBL) | PBL < 1×10-9 Torr | C100R-ACC-CM-COMM | InstInitBLVacuum
| Pressure of each individual waveguide guard vacuums | PWG < 1×10-9 Torr | C100R-ACC-CM-COMM | C#InstInitBLVacuum
| Pressure inside the vacuum vessel at 2.07 K (PINSVAC) | PINSVAC < 1×10-6 Torr | C100R-CMTF-ACTS *update C100R-ACC-CM-COMM to include recording this value | InsVacLeakCheckEndPressure
| All cryomodule interlock, heaters and He liquid level sensor | Verified functional | C100R-CMTF-ACTS *update C100R-ACC-CM-COMM to include recording this value | Various data fields *update traveler to include a single checkbox to record that all interlock, heaters, He liquid level sensor checks are functional